## Current Product List (1.1.17)
DISCLAIMER- Some of the performance values reported as part of the Cold-Climate ASHP Specification are NOT derived from industry standard test procedures or third-party tested/verified (i.e. performance values at 5°F). Performance in some instances may be represented by manufacturer’s engineering data.
Products added to list since previous update highlighted in pink
General Information | [10 empty] | Condition 1 Performance - (47°F/70°F) | [8 empty] | Condition 2 Performance - (17°F/70°F) | [8 empty] | Condition 3 Performance - (5°F/70°F)* | [7 empty] | Pan Heater Data |  |  | OPTIONAL Condition 4 Performance - (X°F/70°F)*
[11 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  | Input Power (kW) |  | COP | [7 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  | COP
Updated: January 20, 2017
Manufacturer | Brand (if applicable) | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | HSPF (Region IV): | SEER | EER (@ 95°F) | ENERGY STAR Certified | Ductless or Ducted | If Ductless, Multi-zone or Single-zone? | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F | COP at Max. Capacity 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F | COP at Max. Capacity X°F
American Standard |  | 6749789 | 4A6V0024A1 | *AM8C0B30V21 | 10 | 19.25 | 13.75 | Yes | Ducted | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 | 11176 | 13000 | 1.58 | 1.84 | 2.08 | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A |  | z
American Standard |  | 6992577 | 4A6V0036A1 | *AM8C0B30V21 | 10 | 20 | 13 | Yes | Ducted | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 | 16688 | 20160 | 2.64 | 3.16 | 1.86 | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z
American Standard |  | 7599436 | 4A6V0036A1 | *AM8C0C48V41 | 10 | 20.75 | 13.5 | Yes | Ducted | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 | 16548 | 19800 | 2.54 | 3 | 1.9 | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A |  | z
American Standard |  | 7125570 | 4A6V0036A1 | *UHMB060ACV3 4TXCB004CC3 | 10 | 18.5 | 12.5 | Yes | Ducted | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 | 16934 | 20300 | 2.82 | 3.36 | 1.76 | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A |  | z
American Standard |  | 6796524 | 4A6V0036A1 | *UD2C080ACV4 4TXCC007CC3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 | 16488 | 19800 | 2.7 | 3.22 | 1.78 | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z
American Standard |  | 6796526 | 4A6V0036A1 | *UD2C100ACV5 4TXCC007CC3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 | 16588 | 19900 | 2.7 | 3.2 | 1.8 | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z
American Standard |  | 7125572 | 4A6V0036A1 | *DHMB060BCV3 4TXFH036CZ3 | 10 | 19.5 | 12.5 | Yes | Ducted | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 | 17034 | 20340 | 2.78 | 3.28 | 1.8 | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z
American Standard |  | 6796528 | 4A6V0036A1 | *UD2C080ACV4 4TXFH036CZ3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 | 16628 | 19900 | 2.66 | 3.16 | 1.84 | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z
American Standard |  | 7125571 | 4A6V0036A1 | *UHMB060ACV3 4TXFH036CZ3 | 10 | 18.75 | 12.5 | Yes | Ducted | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 | 16788 | 20040 | 2.78 | 3.32 | 1.76 | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A |  | z
American Standard |  | 6749791 | 4A6V0048A1 | *AM8C0C48V41 | 10 | 19.25 | 12.5 | Yes | Ducted | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 | 22446 | 26720 | 3.72 | 4.44 | 1.76 | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z
American Standard |  | 7161151 | 4A6V0048A1 | *AM8C0C60V51 | 10 | 19.25 | 12.5 | Yes | Ducted | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 | 22486 | 26780 | 3.64 | 4.34 | 1.8 | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A |  | z
American Standard |  | 6750455 | 4A6V8024A1 | *AM8C0B30V21 | 10 | 18 | 13 | Yes | Ducted | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 | 11176 | 13000 | 1.58 | 1.84 | 2.08 | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A |  | z
American Standard |  | 6750232 | 4A6V8036A1 | *AM8C0C36V31 | 10 | 18 | 13 | Yes | Ducted | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 | 16488 | 19680 | 2.66 | 3.18 | 1.82 | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A |  | z
American Standard |  | 7035709 | 4A6V8036A1 | *DD2C100ACV5 4NXCC005AS3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 | 16828 | 20200 | 2.7 | 3.26 | 1.82 | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A |  | z
American Standard |  | 6796559 | 4A6V8037A1 | *AM8C0B30V21 | 10 | 18 | 13 | Yes | Ducted | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 | 16688 | 20160 | 2.66 | 3.16 | 1.84 | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z
American Standard |  | 6796560 | 4A6V8037A1 | *UD2B080ACV3 4TXCB004CC3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 | 16934 | 20240 | 2.8 | 3.32 | 1.78 | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A |  | z
American Standard |  | 6796562 | 4A6V8037A1 | *UD2C080ACV4 4TXCC007CC3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 | 16488 | 19800 | 2.7 | 3.22 | 1.78 | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z
American Standard |  | 6796563 | 4A6V8037A1 | *UD2C100ACV5 4TXCC007CC3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 | 16588 | 19900 | 2.7 | 3.2 | 1.8 | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z
American Standard |  | 7125581 | 4A6V8037A1 | *DHMB060BCV3 4TXFH036CZ3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 | 17034 | 20340 | 2.78 | 3.28 | 1.8 | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z
American Standard |  | 6796565 | 4A6V8037A1 | *UD2C080ACV4 4TXFH036CZ3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 | 16628 | 19900 | 2.66 | 3.16 | 1.84 | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z
American Standard |  | 6750233 | 4A6V8048A1 | *AM8C0C48V41 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 | 22792 | 27080 | 3.66 | 4.38 | 1.82 | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A |  | z
American Standard |  | 6750457 | 4A6V8049A1 | *AM8C0C48V41 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 | 22446 | 26720 | 3.72 | 4.44 | 1.76 | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z
American Standard | American Standard | 7151530 | 4TXK2709A10N0AA | 4MXW2709A10N0AA | 10 | 27 | 14.5 | Yes | Ductless | Singlezone | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 | 1480 | 8000 | 0.15 | 1.095 | 2.8916 | 2.1412 | 72.73% | 75.25% | Integrated | 72W | Heater on below 34°F | N/A |  | z
American Standard | American Standard | 7151532 | 4TXK2712A10NAA | 4MXW2712A10N0AA | 10 | 25 | 13 | Yes | Ductless | Singlezone | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 | 2100 | 8300 | 0.085 | 1.131 | 7.2406 | 2.1507 | 59.29% | 95.4% | Integrated | 72W | Heater on below 34°F | N/A |  | z
American Standard | American Standard | 7151534 | 4TXK2718A10N0AA | 4MXW2718A10N0AA | 10 | 21 | 12.5 | Yes | Ductless | Singlezone | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 | 2388 | 15400 | 0.42 | 2.29 | 1.6663 | 1.9709 | 66.37% | 78.28% | Integrated | 160W | Heater on below 34°F | N/A |  | z
Carrier | Carrier | 9854622 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 10 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
Carrier | Bryant | 9854623 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 10 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
Carrier | Bryant | 9854627 | 38MGRQ30D--3 | Non-Ducted Indoor Units | 10 | 23.8 | 12.5 | Yes | Ductless | Multizone | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | 9118478 | 38MGRQ48E--3 | Non-Ducted Indoor Units | 10.2 | 22.4 | 12.5 | Yes | Ductless | Multizone | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 | 6577 | 36340 | 1.1 | 5.39 | 1.7523 | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | n/A |  | z
Carrier | Carrier | 9118477 | 38MGRQ48E--3 | Non-Ducted Indoor Units | 10.2 | 22.4 | 12.5 | Yes | Ductless | Multizone | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 | 6577 | 36340 | 1.1 | 5.39 | 1.7523 | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | 8738643 | 38MAQB24R--3 | 619PEQ024BBMA | 10.3 | 20.5 | 13 | Yes | Ductless | Singlezone | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.42 | 2.64 | 1.95 | 2856 | 24030 | 0.295 | 3.98 | 2.83 | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | 9118462 | 38MGRQ18B--3 | Non-Ducted Indoor Units | 10.3 | 22.5 | 12.5 | Yes | Ductless | Multizone | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 | 4752 | 13990 | 0.58 | 1.91 | 2.4012 | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 9118461 | 38MGRQ18B--3 | Non-Ducted Indoor Units | 10.3 | 22.5 | 12.5 | Yes | Ductless | Multizone | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 | 4752 | 13990 | 0.58 | 1.91 | 2.4012 | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | 8856654 | 38MAQB18R--3 | 619REQ018CBMA | 10.5 | 20 | 12.5 | Yes | Ductless | Singlezone | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.4 | 2.55 | 2.06 | 2660 | 19010 | 0.23 | 3.18 | 3.39 | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | 8856652 | 38MAQB18R--3 | Ducted Indoor Units | 10.5 | 19.6 | 12.5 | Yes | Ductless | Singlezone | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 | 5500 | 18000 | 0.67729 | 3.0146 | 2.38 | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | 9118474 | 38MGRQ36D--3 | Non-Ducted Indoor Units | 10.5 | 21.5 | 13.5 | Yes | Ductless | Multizone | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 | 7210 | 36080 | 1.2 | 5.39 | 1.7609 | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 8856653 | 38MAQB18R--3 | Ducted Indoor Units | 10.5 | 19.6 | 12.5 | Yes | Ductless | Singlezone | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 | 5500 | 18000 | 0.67729 | 3.0146 | 2.38 | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 9118473 | 38MGRQ36D--3 | Non-Ducted Indoor Units | 10.5 | 21.5 | 13.5 | Yes | Ductless | Multizone | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 | 7210 | 36080 | 1.2 | 5.39 | 1.7609 | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | 8738646 | 38MAQB09R--3 | 619PEQ009BBMA | 11.2 | 25 | 14.5 | Yes | Ductless | Singlezone | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.55 | 2.74 | 2.26 | 1907 | 10900 | 0.13 | 1.613 | 4.3 | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | 7029861 | 280ANV060000 | FE4ANB006L | 12 | 18 | 12.7 | Yes | Ducted | N/A | 24690 | 55500 | 55500 | 1.75 | 4.2165 | 4.2165 | 4.14 | 3.86 | 3.86 | 24160 | 52500 | 52500 | 2.93 | 6.9351 | 6.9351 | 2.42 | 2.22 | 2.22 | 19480 | 40270 | 2.81 | 5.93 | 2.03 | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A |  | z
Carrier | Bryant | 8738645 | 38MAQB12R--3 | 619PEQ012BBMA | 12 | 22.5 | 12.5 | Yes | Ductless | Singlezone | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.18 | 2.64 | 2.26 | 2030 | 12010 | 0.141 | 1.78 | 4.22 | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | 7029863 | 280ANV048000 | FE4ANB006L | 12.5 | 18.3 | 13.5 | Yes | Ducted | N/A | 24370 | 45500 | 45500 | 1.59 | 3.2386 | 3.2386 | 4.49 | 4.12 | 4.12 | 23840 | 47500 | 47500 | 2.66 | 3.35 | 6.27 | 2.6283 | 2.22 | 2.22 | 19230 | 38070 | 2.55 | 4.97 | 2.21 | 2.24 | 83.67% | 80.15% | N/A |  |  | N/A |  | z
Carrier | Bryant | 7029864 | 280ANV024000 | FE4ANB006L | 13 | 20.5 | 16 | Yes | Ducted | N/A | 14510 | 23600 | 24800 | 0.85 | 1.47 | 1.47 | 5.01 | 4.7 | 4.7 | 13740 | 24800 | 24800 | 1.54 | 2.86 | 2.86 | 2.62 | 2.54 | 2.54 | 10930 | 19630 | 1.47 | 2.77 | 1.73 | 2.08 | 79.15% | 79.15% | N/A |  |  | N/A |  | z
Carrier | Bryant | 7029862 | 280ANV036000 | FE4ANB006L | 13 | 20.5 | 14.5 | Yes | Ducted | N/A | 13340 | 33400 | 33400 | 0.95 | 2.23 | 2.23 | 4.12 | 4.4 | 4.4 | 13250 | 31600 | 31600 | 1.83 | 3.65 | 3.65 | 2.12 | 2.54 | 2.54 | 10670 | 23600 | 1.88 | 3.14 | 1.66 | 2.2 | 70.66% | 74.68% | N/A |  |  | N/A |  | z
Carrier | Carrier | 9854626 | 38MGRQ30D--3 | Non-Ducted Indoor Units | 10 | 23.8 | 12.5 | Yes | Ductless | Multizone | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 7992954 | 38GRQB09---301 | 40GRQB09H--301 | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
Carrier | Carrier | 7992956 | 38GRQB12---301 | 40GRQB12H--301 | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
Carrier | Carrier | 7992958 | 38GRQB18---301 | 40GRQB18H--301 | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
Carrier | Carrier | 8738638 | 38MAQB24R--3 | 40MAQB24B--3 | 10.3 | 20.5 | 13 | Yes | Ductless | Singlezone | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.42 | 2.64 | 1.95 | 2856 | 24030 | 0.295 | 3.98 | 2.83 | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier | 8856655 | 38MAQB18R--3 | 40MBQB18C--3 | 10.5 | 20 | 12.5 | Yes | Ductless | Singlezone | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.4 | 2.55 | 2.06 | 2660 | 19010 | 0.23 | 3.18 | 3.39 | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier | 8738635 | 38MAQB09R--3 | 40MAQB09B--3 | 11.2 | 25 | 14.5 | Yes | Ductless | Singlezone | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.55 | 2.74 | 2.26 | 1907 | 10900 | 0.13 | 1.613 | 4.3 | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier | 8738636 | 38MAQB12R--3 | 40MAQB12B--3 | 12 | 22.5 | 12.5 | Yes | Ductless | Singlezone | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.18 | 2.64 | 2.26 | 2030 | 12010 | 0.141 | 1.78 | 4.22 | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Daikin |  | 3208523 | RXG15HVJU | FTXG15HVJU | 10 | 21 | 12.9 | Yes | Ductless | Single-zone | 4668 | 18000 | 21280 | 0.234 | 1.32 | 2.16 | 5.85 | 3.99 | 2.89 | 3003 | 11100 | 14340 | 0.203 | 1.08 | 1.87 | 4.34 | 3 | 2.25 | 2330 | 11150 | 0.19 | 1.75 | 3.59 | 1.87 | 52.4% | 77.75% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 8750 |  | 1.67 |  | 1.54
Daikin |  | 8849535 | 2MXL18QMVJU | Non-Ducted Indoor Units | 10.3 | 17 | 12.7 | Yes | Ductless | Multi-zone | 7710 | 18940 | 36000 | 0.47 | 1.32 | 3.17 | 4.81 | 4.21 | 3.33 | 5020 | 12330 | 23480 | 0.41 | 1.15 | 2.77 | 3.59 | 3.14 | 2.48 | 4050 | 18930 | 0.39 | 2.62 | 3.04 | 2.12 | 52.58% | 80.62% | N/A |  |  | N/A |  | z
Daikin |  | 3208522 | RXG12HVJU | FTXG12HVJU | 10.55 | 24.2 | 14 | Yes | Ductless | Single-zone | 4668 | 16000 | 19130 | 0.224 | 1.16 | 2.14 | 6.11 | 4.04 | 2.62 | 3003 | 10400 | 12920 | 0.192 | 0.98 | 1.78 | 4.58 | 3.1 | 2.13 | 2330 | 10040 | 0.181 | 1.67 | 3.77 | 1.76 | 52.48% | 77.71% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7880 |  | 1.58 |  | 1.46
Daikin |  | 5265758 | RXS24LVJU | FTXS24LVJU | 10.6 | 20 | 12.5 | Yes | Ductless | Single-zone | 7800 | 25400 | 31400 | 0.54 | 2.21 | 2.75 | 4.25 | 3.37 | 3.34 | 4260 | 13781 | 17041 | 0.37 | 1.54 | 1.91 | 3.34 | 2.63 | 2.61 | 3507 | 14028 | 0.36 | 1.82 | 2.89 | 2.26 | 44.68% | 82.32% | Accessory (KEH041A43) |  | Temp. below 23 degrees | 0 | 3055 | z | 12220 | 0.35 | 1.77 | 2.59 | 2.03
Daikin |  | 8103542 | 2MXS18NMVJU | Non-Ducted Indoor Units | 10.7 | 18.9 | 12.5 | Yes | Ductless | Multi-zone | 4900 | 18900 | 25000 | 0.29 | 1.26 | 1.69 | 4.94 | 4.4 | 4.34 | 3800 | 12780 | 16910 | 0.29 | 1.11 | 1.49 | 3.83 | 3.37 | 3.33 | 3190 | 13150 | 0.29 | 1.4 | 3.21 | 2.76 | 52.6% | 77.76% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 2910 | z | 11580 | 0.29 | 1.36 | 2.93 | 2.5
Daikin |  | 5265757 | RXS18LVJU | FTXS18LVJU | 11 | 20.3 | 12.7 | Yes | Ductless | Single-zone | 5800 | 21600 | 26700 | 0.41 | 1.71 | 2.12 | 4.17 | 3.7 | 3.7 | 3149 | 11725 | 14485 | 0.28 | 1.19 | 1.47 | 3.26 | 2.89 | 2.89 | 2592 | 11924 | 0.27 | 1.4 | 2.82 | 2.49 | 44.66% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 10387 | 0.26 | 1.36 | 2.53 | 2.24
Daikin |  | 3208521 | RXG09HVJU | FTXG09HVJU | 11 | 26.1 | 15.8 | Yes | Ductless | Single-zone | 4668 | 12000 | 18670 | 0.224 | 0.78 | 1.94 | 6.11 | 4.51 | 2.82 | 3003 | 8100 | 12170 | 0.194 | 0.72 | 1.68 | 4.54 | 3.3 | 2.12 | 2330 | 9460 | 0.182 | 1.57 | 3.75 | 1.77 | 50.67% | 77.73% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7430 |  | 1.49 |  | 1.46
Daikin |  | 8849445 | RXL15QMVJU | FVXS15NVJU | 11.3 | 20 | 12.5 | Yes | Ductless | Single-zone | 5814 | 18056 | 23884 | 0.34 | 1.401 | 1.809 | 5.01 | 3.78 | 3.87 | 3784 | 11751 | 19414 | 0.297 | 1.222 | 2.105 | 3.73 | 2.82 | 2.7 | 2958 | 18015 | 0.279 | 2.198 | 3.11 | 2.4 | 75.43% | 92.79% | N/A |  |  | N/A |  | z
Daikin |  | 5265756 | RXS15LVJU | FTXS15LVJU | 11.6 | 20.6 | 14.4 | Yes | Ductless | Single-zone | 5800 | 18000 | 22300 | 0.39 | 1.32 | 1.64 | 4.35 | 4 | 3.97 | 3149 | 9780 | 12114 | 0.27 | 0.92 | 1.14 | 3.4 | 3.13 | 3.11 | 2592 | 9972 | 0.26 | 1.09 | 2.94 | 2.69 | 44.72% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 8687 | 0.25 | 1.06 | 2.64 | 2.41
Daikin |  | 8849459 | RXL09QMVJU | FVXS09NVJU | 11.7 | 20 | 12.5 | Yes | Ductless | Single-zone | 4446 | 10089 | 14330 | 0.24 | 0.721 | 1.356 | 5.43 | 4.1 | 3.1 | 2893 | 6565 | 11082 | 0.21 | 0.629 | 1.378 | 4.04 | 3.06 | 2.36 | 2262 | 10065 | 0.197 | 1.384 | 3.37 | 2.13 | 70.24% | 90.82% | N/A |  |  | N/A |  | z
Daikin |  | 8849458 | RXL12QMVJU | FTX12NMVJU | 12 | 20 | 12.5 | Yes | Ductless | Single-zone | 4446 | 13679 | 18766 | 0.24 | 1.026 | 1.562 | 5.43 | 3.91 | 3.52 | 2893 | 8902 | 15388 | 0.21 | 0.895 | 1.789 | 4.04 | 2.92 | 2.52 | 2262 | 14330 | 0.197 | 1.86 | 3.37 | 2.26 | 76.36% | 93.12% | N/A |  |  | N/A |  | z
Daikin |  | 5265753 | RXS09LVJU | FTXS09LVJU | 12.5 | 24.5 | 15.3 | Yes | Ductless | Single-zone | 4400 | 12000 | 15600 | 0.22 | 0.79 | 1.27 | 5.99 | 4.45 | 3.6 | 2408 | 6520 | 8465 | 0.15 | 0.55 | 0.88 | 4.72 | 3.48 | 2.81 | 1982 | 6968 | 0.14 | 0.84 | 4.08 | 2.43 | 44.67% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1727 | z | 6070 | 0.14 | 0.82 | 3.66 | 2.18
Daikin |  | 5265755 | RXS12LVJU | FTXS12LVJU | 12.5 | 23 | 12.8 | Yes | Ductless | Single-zone | 4800 | 14400 | 18000 | 0.22 | 0.97 | 1.27 | 6.53 | 4.35 | 4.15 | 2593 | 7816 | 9780 | 0.15 | 0.67 | 0.88 | 5.08 | 3.4 | 3.25 | 2135 | 8051 | 0.14 | 0.84 | 4.39 | 2.81 | 44.73% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1860 | z | 7013 | 0.14 | 0.82 | 3.94 | 2.52
Daikin |  | 8103869 | 3MXS24NMVJU | Non-Ducted Indoor Units | 12.5 | 17.9 | 12.7 | Yes | Ductless | Multi-zone | 8500 | 24000 | 36000 | 0.43 | 1.46 | 2.97 | 5.79 | 4.82 | 3.55 | 6570 | 16230 | 24350 | 0.43 | 1.29 | 2.62 | 4.48 | 3.69 | 2.72 | 5500 | 18930 | 0.43 | 2.46 | 3.75 | 2.26 | 52.58% | 77.74% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 5020 | z | 16670 | 0.43 | 2.39 | 3.42 | 2.05
Daikin |  | 8849533 | RXL09QMVJU | FTX09NMVJU | 12.5 | 20 | 12.5 | Yes | Ductless | Single-zone | 4446 | 10942 | 16036 | 0.23 | 0.761 | 1.701 | 5.67 | 4.21 | 2.76 | 2893 | 7121 | 12136 | 0.201 | 0.664 | 1.642 | 4.22 | 3.14 | 2.17 | 2262 | 10918 | 0.189 | 1.623 | 3.51 | 1.97 | 68.08% | 89.96% | N/A |  |  | N/A |  | z
Daikin |  | 8849330 | RXL15QMVJU | FTX15NMVJU | 12.5 | 20 | 13 | Yes | Ductless | Single-zone | 5814 | 18295 | 24566 | 0.39 | 1.341 | 2.307 | 4.37 | 4 | 3.12 | 3784 | 11904 | 19755 | 0.341 | 1.17 | 2.361 | 3.25 | 2.98 | 2.45 | 2958 | 18254 | 0.32 | 2.361 | 2.71 | 2.27 | 74.31% | 92.4% | N/A |  |  | N/A |  | z
Daikin |  | 8849539 | 3MXL24QMVJU | Non-Ducted Indoor Units | 12.5 | 17.9 | 12.7 | Yes | Ductless | Multi-zone | 7720 | 24000 | 41000 | 0.44 | 1.54 | 3.52 | 5.14 | 4.57 | 3.41 | 5030 | 15670 | 26780 | 0.38 | 1.35 | 3.08 | 3.88 | 3.4 | 2.55 | 4060 | 21600 | 0.36 | 2.92 | 3.31 | 2.17 | 52.68% | 80.66% | N/A |  |  | N/A |  | z
Friedrich |  | 7000021 | MR09Y3J | MW09Y3J | 11 | 21.5 | 13.3 | Yes | Ductless | Single-zone | 3000 | 10800 | 17061 | 0.2 | 0.7 | 1.39 | 4.34 | 4.52 | 3.6 | 2700 | 5880 | 15355 | 0.27 | 0.56 | 1.9 | 2.89 | 3.08 | 2.37 | 2070 | 11942.7 | 0.28 | 1.95 | 2.16 | 1.79 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z
Friedrich |  | 7000022 | MR12Y3J | MW12Y3J | 11 | 21.5 | 12.5 | Yes | Ductless | Single-zone | 3000 | 13300 | 22178 | 0.19 | 1 | 2.08 | 4.49 | 3.9 | 3.12 | 2700 | 6880 | 19960 | 0.26 | 0.81 | 2.85 | 3.04 | 2.49 | 2.05 | 2070 | 15524.6 | 0.266 | 2.91 | 2.28 | 2 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z
Friedrich |  | 7012589 | MR24Y3J | MW24Y3J | 11 | 21.5 | 12.5 | Yes | Ductless | Single-zone | 6200 | 27000 | 38898 | 0.53 | 2.38 | 4.19 | 3.43 | 3.4 | 2.72 | 5456 | 17240 | 34230 | 0.58 | 1.92 | 4.61 | 2.76 | 2.63 | 2.18 | 4278 | 27228.6 | 0.6 | 4.42 | 2.08 | 1.8 | 70% | 79.55% | N/A |  |  | N/A |  | z
Fujitsu |  | 8033584 | AOU18RLXFZH | Non-Ducted Indoor Units | 10.3 | 21.5 | 13.5 | Yes | Ductless | Multi-zone | 6200 | 22000 | 24400 | 0.52 | 1.7 | 2.02 | 3.85 | 3.8 | 3.54 | 6619 | 14200 | 23500 | 0.81 | 1.6 | 3.18 | 2.4 | 2.6 | 2.16 | 6210 | 22000 | 0.89 | 3.49 | 2.04 | 1.85 | 90.16% | 93.62% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3378 | z | 12000 | 0.55 | 2.14 | 1.8 | 1.64
Fujitsu |  | 8033586 | AOU24RLXFZH | Non-Ducted Indoor Units | 10.3 | 20 | 13.3 | Yes | Ductless | Multi-zone | 6200 | 25000 | 29800 | 0.5 | 1.81 | 2.85 | 4 | 4.04 | 3.06 | 6005 | 15400 | 26000 | 0.62 | 1.73 | 3.57 | 2.84 | 2.6 | 2.13 | 5869 | 25500 | 0.62 | 3.57 | 2.77 | 2.09 | 85.57% | 98.08% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3207 | z | 13500 | 0.43 | 2.44 | 2.19 | 1.62
Fujitsu |  | 8908615 | AOU36RLXFZH | Non-Ducted Indoor Units | 10.3 | 20 | 13 | Yes | Ductless | Multi-zone | 12000 | 36400 | 42000 | 0.7 | 2.67 | 3.29 | 5.02 | 4 | 3.74 | 11212 | 21400 | 39341 | 1.09 | 2.38 | 5.13 | 3.02 | 2.64 | 2.25 | 10376 | 36407 | 1.12 | 5.28 | 2.72 | 2.02 | 86.68% | 92.54% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 6301 | z | 22110 | 0.91 | 3.59 | 2.03 | 1.81
Fujitsu |  | 8779045 | AOU18RLXFWH | ASU18RLF | 10.4 | 20 | 13.3 | Yes | Ductless | Single-zone | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 | 5485 | 14600 | 22759 | 0.57 | 1.42 | 3 | 2.82 | 3.02 | 2.22 | 5205 | 21600 | 0.54 | 2.75 | 2.82 | 2.3 | 74.48% | 94.91% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 4317 | z | 17913 | 0.42 | 1.83 | 3.01 | 2.87
Fujitsu |  | 8718495 | AOU18RLXFW1 | ASU18RLF | 10.5 | 20 | 13.3 | Yes | Ductless | Single-zone | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 | 5485 | 14600 | 22759 | 0.42 | 1.39 | 2.85 | 3.83 | 3.08 | 2.34 | 5205 | 21600 | 0.39 | 2.6 | 3.91 | 2.43 | 74.48% | 94.91% | N/A |  |  | -5 | 4745 | z | 19688 | 0.33 | 2.22 | 4.21 | 2.6
Fujitsu |  | 6937311 | AOU15RLFFH | AGU15RLF | 11 | 20.3 | 12.5 | Yes | Ductless | Single-zone | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5 | 3.68 | 3.03 | 2832 | 11600 | 19000 | 0.47 | 1.3 | 3.04 | 1.77 | 2.62 | 1.83 | 2798 | 18500 | 0.41 | 3.06 | 2 | 1.77 | 88.94% | 97.37% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2320 | z | 15500 | 0.41 | 2.93 | 1.66 | 1.55
Fujitsu |  | 6936997 | AOU15RLFF | AGU15RLF | 11.2 | 20.3 | 12.5 | Yes | Ductless | Single-zone | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5 | 3.68 | 3.03 | 2832 | 11600 | 19000 | 0.32 | 1.3 | 2.89 | 2.59 | 2.62 | 1.93 | 2798 | 18500 | 0.26 | 2.91 | 3.15 | 1.86 | 88.94% | 97.37% | N/A |  |  | -5 | 2593 | z | 17500 | 0.26 | 2.86 | 2.92 | 1.79
Fujitsu |  | 6937310 | AOU12RLFFH | AGU12RLF | 11.3 | 22.7 | 13.1 | Yes | Ductless | Single-zone | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5 | 3.87 | 3.1 | 2457 | 10600 | 15000 | 0.39 | 1.19 | 2.32 | 1.85 | 2.6 | 1.89 | 2423 | 15000 | 0.39 | 2.32 | 1.82 | 1.89 | 76.92% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2252 | z | 14000 | 0.48 | 2.99 | 1.38 | 1.37
Fujitsu |  | 5751314 | AOU12RLFC | ARU12RLF | 11.5 | 20 | 12.8 | Yes | Ductless | Single-zone | 3100 | 16000 | 19400 | 0.15 | 1.3 | 2 | 6 | 3.61 | 2.85 | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 | 2647 | 16500 | 0.18 | 2.25 | 4.31 | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2.32 | 3.75 | 1.9
Fujitsu |  | 6936996 | AOU12RLFF | AGU12RLF | 11.6 | 22.7 | 13.1 | Yes | Ductless | Single-zone | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5 | 3.87 | 3.1 | 2457 | 10600 | 15000 | 0.24 | 1.19 | 2.17 | 3 | 2.6 | 2.02 | 2423 | 15000 | 0.24 | 2.17 | 2.96 | 2.02 | 76.92% | 100% | N/A |  |  | -5 | 2115 | z | 13000 | 0.22 | 2.06 | 2.82 | 1.85
Fujitsu |  | 5063326 | AOU12RLS2 | ASU12RLS2 | 12 | 25 | 13.8 | Yes | Ductless | Single-zone | 3100 | 16000 | 22110 | 0.2 | 1.2 | 2 | 4.5 | 3.91 | 3.24 | 2491 | 10200 | 17900 | 0.2 | 1.1 | 2 | 3.65 | 2.72 | 2.63 | 2320 | 16500 | 0.21 | 2.1 | 3.24 | 2.34 | 74.63% | 92.18% | N/A |  |  | -5 | 2081 | z | 15000 | 0.21 | 2.1 | 2.9 | 2.1
Fujitsu |  | 5751312 | AOU9RLFC | ARU9RLF | 12.2 | 21.5 | 14.5 | Yes | Ductless | Single-zone | 3100 | 12000 | 18000 | 0.15 | 0.85 | 1.8 | 6 | 4.14 | 2.93 | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 | 2610 | 15000 | 0.15 | 1.87 | 5.11 | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 1.92 | 4.54 | 2.14
Fujitsu |  | 5751313 | AOU12RLFC | AUU12RLF | 12.2 | 21.9 | 12.8 | Yes | Ductless | Single-zone | 3100 | 16000 | 19400 | 0.15 | 1.44 | 2 | 6 | 3.26 | 2.85 | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 | 2647 | 16500 | 0.18 | 2.25 | 4.31 | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2.32 | 3.75 | 1.9
Fujitsu |  | 6937309 | AOU9RLFFH | AGU9RLF | 12.4 | 26 | 16 | Yes | Ductless | Single-zone | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5 | 4.71 | 2.99 | 2320 | 7500 | 14000 | 0.35 | 0.78 | 1.97 | 1.94 | 2.8 | 2.08 | 2115 | 14000 | 0.34 | 2.25 | 1.82 | 1.82 | 74.47% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1843 | z | 11000 | 0.38 | 2.07 | 1.42 | 1.56
Fujitsu |  | 5063325 | AOU9RLS2 | ASU9RLS2 | 12.5 | 27.2 | 16.1 | Yes | Ductless | Single-zone | 3100 | 12000 | 22000 | 0.2 | 0.8 | 1.99 | 4.5 | 4.4 | 3.24 | 2320 | 9400 | 16400 | 0.2 | 1.09 | 1.97 | 3.4 | 2.54 | 2.45 | 2150 | 15000 | 0.21 | 2.06 | 3 | 2.18 | 68.18% | 91.46% | N/A |  |  | -5 | 1945 | z | 13500 | 0.21 | 2.05 | 2.71 | 2
Fujitsu |  | 6936995 | AOU9RLFF | AGU9RLF | 12.6 | 26 | 16 | Yes | Ductless | Single-zone | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5 | 4.71 | 2.99 | 2320 | 7500 | 14000 | 0.2 | 0.78 | 1.82 | 3.4 | 2.8 | 2.25 | 2115 | 14000 | 0.19 | 2.1 | 3.26 | 1.95 | 74.47% | 100% | N/A |  |  | -5 | 2047 | z | 12500 | 0.22 | 2 | 2.73 | 1.83
Fujitsu |  | 5751311 | AOU9RLFC | AUU9RLF | 13 | 24 | 14.5 | Yes | Ductless | Single-zone | 3100 | 12000 | 18000 | 0.15 | 0.89 | 1.8 | 6 | 3.95 | 2.93 | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 | 2610 | 15000 | 0.15 | 1.87 | 5.11 | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 1.92 | 4.54 | 2.14
Fujitsu |  | 7993245 | AOU15RLS3H | ASU15RLS3 | 13.3 | 25.3 | 13.9 | Yes | Ductless | Single-zone | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.59 | 3.2 | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 | 2696 | 20500 | 0.36 | 2.9 | 2.19 | 2.07 | 85.77% | 95.35% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2081 | z | 16000 | 0.37 | 2.88 | 1.65 | 1.63
Fujitsu |  | 7993243 | AOU15RLS3 | ASU15RLS3 | 13.4 | 25.3 | 13.9 | Yes | Ductless | Single-zone | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.59 | 3.2 | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 | 2696 | 20500 | 0.21 | 2.75 | 3.76 | 2.18 | 85.77% | 95.35% | N/A |  |  | -5 | 2388 | z | 18500 | 0.21 | 2.74 | 3.33 | 1.98
Fujitsu |  | 7993244 | AOU12RLS3H | ASU12RLS3 | 13.8 | 29.3 | 15.2 | Yes | Ductless | Single-zone | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5 | 4.64 | 3.34 | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 | 2320 | 16500 | 0.37 | 2.25 | 1.84 | 2.15 | 74.63% | 94.29% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1638 | z | 11500 | 0.38 | 2.23 | 1.26 | 1.51
Fujitsu |  | 7993242 | AOU12RLS3 | ASU12RLS3 | 14 | 29.3 | 15.2 | Yes | Ductless | Single-zone | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5 | 4.64 | 3.34 | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 | 2320 | 16500 | 0.22 | 2.1 | 3.09 | 2.3 | 74.63% | 94.29% | N/A |  |  | -5 | 2081 | z | 15000 | 0.22 | 2.09 | 2.77 | 2.1
Fujitsu |  | 8004700 | AOU9RLS3H | ASU9RLS3 | 14 | 33 | 18 | Yes | Ductless | Single-zone | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.33 | 3.34 | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 | 2150 | 15000 | 0.37 | 2.25 | 1.7 | 1.95 | 68.18% | 93.75% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1535 | z | 11000 | 0.38 | 2.23 | 1.18 | 1.44
Fujitsu |  | 8004699 | AOU9RLS3 | ASU9RLS3 | 14.2 | 33 | 18 | Yes | Ductless | Single-zone | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.33 | 3.34 | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 | 2150 | 15000 | 0.22 | 2.1 | 2.86 | 2.09 | 68.18% | 93.75% | N/A |  |  | -5 | 1945 | z | 13500 | 0.22 | 2.09 | 2.59 | 1.89
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038626 | WSM09MH20S/O | WSM09MH20S/I | 10 | 20.5 | 14 | Yes | Ductless | Singlezone | 2908 | 9800 | 11602.2672 | 0.2454 | 0.89757 | 1.1766 | 3.4729 | 3.1999 | 2.8899 | 6300 | 6300 | 7979.9856 | 0.68896 | 0.68896 | 1.0929 | 2.6799 | 2.6799 | 2.1399 | 6600 | 6700 | 1.0075 | 1.0122 | 1.9199 | 1.9399 | 57.75% | 83.96% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038628 | WSM18MH20S/O | WSM18MH20S/I | 10 | 22 | 13 | Yes | Ductless | Singlezone | 6093 | 18000 | 19146 | 0.37915 | 1.6695 | 1.5896 | 4.7097 | 3.1599 | 3.5299 | 11100 | 11100 | 12396 | 1.1787 | 1.1787 | 1.5013 | 2.7599 | 2.7599 | 2.4199 | 10460.09 | 12500 | 1.5252 | 2.0816 | 2.0099 | 1.7599 | 65.29% | 100.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038629 | WSM24MH20S/O | WSM24MH20S/I | 10 | 20 | 12.5 | Yes | Ductless | Singlezone | 10271 | 25000 | 27303 | 0.64679 | 2.4588 | 3.5723 | 4.654 | 2.9799 | 2.2399 | 16000 | 16000 | 18330 | 1.9062 | 1.9062 | 2.798 | 2.4599 | 2.4599 | 1.9199 | 14800 | 15815 | 2.4786 | 2.6336 | 1.7499 | 1.7599 | 57.92% | 86.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038618 | WUHO09KW25S | WUHI09KHW | 11.2 | 25 | 14.5 | Yes | Ductless | Singlezone | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 | 10720 | 11680 | 1.7621 | 1.945 | 1.7829 | 1.7599 | 76.02% | 92.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038621 | WUHO24KW20S | WUHI24KHW | 11.5 | 20.5 | 13 | Yes | Ductless | Singlezone | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.0298 | 3.5999 | 2.7199 | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.7599 | 2.7599 | 1.9499 | 23260 | 24590 | 3.8298 | 3.9817 | 1.7799 | 1.8099 | 82.85% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis | 9038619 | WUHO12KW22S | WUHI12KHW | 12 | 22.5 | 12.5 | Yes | Ductless | Singlezone | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.2998 | 3.5399 | 3.2699 | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.6399 | 2.6399 | 2.2099 | 11800 | 12010 | 1.9762 | 1.9555 | 1.7499 | 1.7999 | 77.14% | 84.94% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Haier | Haier | 6970203 | HSU09VHG(DB)-W | HSU09VHG(DB)-G | 10 | 18 | 13 | Yes | Ductless | Single Zone | 4000 | 9000 | 10140 | 0.27 | 0.65 | 0.82 | 4.342 | 4.509 | 3.6242 | 3200 | 5600 | 7190 | 0.27 | 0.52 | 0.64 | 3.4736 | 3.1563 | 3.2926 | 2800 | 6000 | 0.27 | 0.75 | 3.0394 | 2.3447 | 59.17% | 83.45% | N/A |  |  | N/A |  | z
Haier | Haier | 6970204 | HSU12VHG(DB)-W | HSU12VHG(DB)-G | 10 | 20 | 13 | Yes | Ductless | Single-zone | 4780 | 12600 | 14190 | 0.271 | 0.97 | 1.12 | 5.16 | 3.8 | 3.71 | 3750 | 9000 | 10070 | 0.37 | 1.12 | 1.2 | 2.91 | 2.34 | 2.45 | 2380 | 6930 | 0.24 | 0.88 | 2.82 | 2.3 | 48.84% | 68.82% | N/A |  |  | N/A |  | z
Haier | Haier | 8028525 | 1U24ES2VHA | AW24ES2VHA | 10 | 20 | 12.5 | Yes | Ductless | Single-zone | 6800 | 27700 | 34800 | 0.55 | 2.35 | 3.3 | 3.62 | 3.45 | 3.09 | 5800 | 18500 | 26000 | 0.58 | 1.9 | 3.25 | 2.93 | 2.85 | 2.35 | 4700 | 20500 | 0.55 | 2.8 | 2.51 | 2.15 | 58.91% | 78.85% | N/A |  |  | N/A |  | z
Haier | Haier | 8862057 | 1U18EH2VHA | AW18EH2VHA | 10 | 20 | 12.5 | Yes | Ductless | Single-zone | 6800 | 20400 | 26400 | 0.55 | 1.64 | 3.1 | 3.624 | 3.646 | 2.496 | 5800 | 18500 | 20400 | 0.58 | 1.9 | 2.95 | 2.931 | 2.854 | 2.027 | 4700 | 20400 | 0.55 | 3.15 | 2.505 | 1.898 | 77.27% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
Haier | Haier | 8021588 | 1U12ES2VHA | AW12ES2VHA | 11 | 23 | 12.5 | Yes | Ductless | Single-zone | 4100 | 16000 | 19800 | 0.225 | 1.25 | 1.66 | 5.33 | 3.75 | 3.49 | 3550 | 12220 | 13120 | 0.33 | 1.19 | 1.25 | 3.11 | 3 | 3.07 | 2960 | 10160 | 0.3 | 1.21 | 2.85 | 2.46 | 51.31% | 77.44% | N/A |  |  | N/A |  | z
Haier | Haier | 8028490 | 1U18ES2VHA | AW18ES2VHA | 11 | 21 | 12.6 | Yes | Ductless | Single-zone | 5400 | 22000 | 26400 | 0.4 | 1.83 | 2.9 | 3.96 | 3.52 | 2.67 | 4500 | 14000 | 19600 | 0.45 | 1.5 | 2.7 | 2.93 | 2.74 | 2.13 | 3800 | 14900 | 0.43 | 2.1 | 2.59 | 2.08 | 56.44% | 76.02% | N/A |  |  | N/A |  | z
Haier | Haier | 8028528 | 1U09ES2VHA | AW09ES2VHA | 12 | 23.5 | 14.5 | Yes | Ductless | Single-zone | 4000 | 10000 | 15000 | 0.25 | 0.65 | 1.2 | 4.69 | 4.51 | 3.66 | 3200 | 7400 | 10800 | 0.27 | 0.63 | 1.1 | 3.54 | 3.44 | 2.88 | 2800 | 10000 | 0.26 | 1.18 | 3.16 | 2.48 | 66.67% | 92.59% | N/A |  |  | N/A |  | z
Haier | Haier | 8862052 | 1U12EH2VHA | AW12EH2VHA | 12 | 25 | 13 | Yes | Ductless | Single-zone | 4100 | 16500 | 22200 | 0.225 | 1.345 | 1.69 | 5.341 | 3.595 | 3.85 | 3200 | 10000 | 16500 | 0.33 | 1.185 | 1.595 | 2.842 | 2.473 | 3.032 | 2900 | 16500 | 0.3 | 2.152 | 2.833 | 2.247 | 74.32% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
Haier | Haier | 8862047 | 1U09EH2VHA | AW09EH2VHA | 13 | 28 | 15.5 | Yes | Ductless | Single-zone | 4000 | 12000 | 22000 | 0.245 | 0.9 | 1.65 | 4.785 | 3.908 | 3.908 | 3100 | 9000 | 12000 | 0.26 | 0.82 | 1.18 | 3.494 | 3.217 | 2.981 | 2800 | 12000 | 0.26 | 1.58 | 3.156 | 2.226 | 54.55% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
International Comfort Products | ARCOAIRE | 8177085 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | COMFORTMAKER | 8177087 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3001 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | DAY & NIGHT | 8177084 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3002 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | HEIL | 8177081 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3003 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | KEEPRITE | 8177082 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3004 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | KENMORE | 8177086 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3005 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | TEMPSTAR | 8177083 | DLCAHB09K1A | DLFAHH09K1A | 10.3 | 30.5 | 15.7 | Yes | Ductless | Single-zone | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 | 2388 | 10488 | 0.4 | 1.553 | 1.749 | 1.979 | 79.21% | 79.21% | Integrated | 3006 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | ARCOAIRE | 8177094 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2994 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | COMFORTMAKER | 8177096 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2995 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | DAY & NIGHT | 8177093 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2996 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | HEIL | 8177090 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2997 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | KEEPRITE | 8177091 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2998 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | KENMORE | 8177095 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 2999 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | TEMPSTAR | 8177092 | DLCAHB12K1A | DLFAHH12K1A | 10.3 | 23 | 12.7 | Yes | Ductless | Single-zone | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 | 3071 | 13000 | 0.4 | 1.38 | 2.25 | 2.76 | 100% | 100% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | ARCOAIRE | 8177103 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | COMFORTMAKER | 8177105 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3001 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | DAY & NIGHT | 8177102 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3002 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | HEIL | 8177099 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3003 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | KEEPRITE | 8177100 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3004 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | KENMORE | 8177104 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3005 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | TEMPSTAR | 8177101 | DLCAHB18K1A | DLFAHH18K1A | 10.3 | 21 | 12.5 | Yes | Ductless | Single-zone | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 | 3753 | 19190 | 0.55 | 1.97 | 1.999 | 2.85 | 78.12% | 78.12% | Integrated | 3006 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
Lennox Industries, Inc. | Lennox | 8898934 | MLA012S4S-1P | MMDA012S4-1P | 10 | 19 | 12.5 | Yes | Ductless | Singlezone | 3752 | 12000 | 17021 | 0.189 | 0.961 | 1.692 | 5.818 | 3.6596 | 2.9482 | 3292 | 8500 | 12986 | 0.232 | 0.966 | 2.028 | 4.1586 | 2.5788 | 1.8766 | 2718 | 12341 | 0.205 | 2.031 | 3.8857 | 1.7808 | 72.5% | 95.03% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 8898935 | MLA012S4S-1P | MWMA012S4-1P | 10 | 22 | 12.5 | Yes | Ductless | Singlezone | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 | 2562 | 12038 | 0.203 | 1.972 | 3.6988 | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 8898941 | MLA024S4S-1P | MWMA024S4-1P | 10 | 20 | 12.5 | Yes | Ductless | Singlezone | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 | 5082 | 26030 | 0.487 | 4.29 | 3.0583 | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 9920041 | MLA012S4S-1P | MWMA012S4-2P | 10 | 22 | 12.5 | Yes | Ductless | Singlezone | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 | 2562 | 12038 | 0.203 | 1.972 | 3.6988 | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Lennox Industries, Inc. | Lennox | 9920047 | MLA024S4S-1P | MWMA024S4-2P | 10 | 20 | 12.5 | Yes | Ductless | Singlezone | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 | 5082 | 26030 | 0.487 | 4.29 | 3.0583 | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Lennox Industries, Inc. | Lennox | 8994418 | MLA030S4M-1P | non-ducted indoor units | 10.4 | 22 | 13 | Yes | Ductless | Multizone | 5820 | 28000 | 37720 | 0.895 | 2.345 | 3.475 | 1.9058 | 3.4994 | 3.1812 | 5411 | 18000 | 31054 | 0.924 | 1.925 | 4.176 | 1.7162 | 2.7404 | 2.1794 | 5145 | 28160 | 1.008 | 4.041 | 1.4959 | 2.0423 | 74.66% | 90.68% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 8994421 | MLA036S4M-1P | non-ducted indoor units | 10.5 | 21.5 | 13.5 | Yes | Ductless | Multizone | 7210 | 36000 | 50350 | 1.02 | 2.777 | 4.64 | 2.0716 | 3.7993 | 3.1802 | 6845 | 23200 | 38125 | 1.091 | 2.446 | 5.502 | 1.8387 | 2.7797 | 2.0308 | 6425 | 36000 | 1.146 | 5.379 | 1.6431 | 1.9614 | 71.5% | 94.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 8898932 | MLA009S4S-1P | MWMA009S4-1P | 10.5 | 24 | 14.5 | Yes | Ductless | Singlezone | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 | 1925 | 10830 | 0.172 | 1.7 | 3.28 | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | 9920038 | MLA009S4S-1P | MWMA009S4-2P | 10.5 | 24 | 14.5 | Yes | Ductless | Singlezone | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 | 1925 | 10830 | 0.172 | 1.7 | 3.28 | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
LG |  | 8111355 | LMU30CHV | Non-Ducted Indoor Units | 10 | 22 | 13 | Yes | Ductless | Multi-zone | 9240 | 32000 | 38400 | 1.043 | 2.49 | 3.486 | 2.6 | 3.8 | 3.2 | 5658 | 19600 | 26739 | 0.882 | 2.1 | 2.55 | 1.9 | 2.7 | 3.1 | 4446 | 20622 | 0.84 | 2.42 | 1.6 | 2.5 | 53.7% | 77.12% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7180063 | LMU36CHV | Non-Ducted Indoor Units | 10 | 22 | 13 | Yes | Ductless | Multi-zone | 9240 | 36000 | 41600 | 1.127 | 2.74 | 3.836 | 2.4 | 3.9 | 3.2 | 5658 | 20000 | 29105 | 0.924 | 2.24 | 2.79 | 1.8 | 2.6 | 3.1 | 4446 | 22057 | 0.868 | 2.6 | 1.5 | 2.5 | 53.02% | 75.78% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 8111358 | LMU480HV | Non-Ducted Indoor Units | 10 | 19.5 | 12.5 | Yes | Ductless | Multi-zone | 15840 | 54000 | 61000 | 1.419 | 4.32 | 6.02 | 3.3 | 3.7 | 3 | 9996 | 34080 | 49014 | 0.993 | 3.02 | 5.07 | 3 | 3.3 | 2.8 | 8076 | 38900 | 0.851 | 4.52 | 2.8 | 2.5 | 63.77% | 79.37% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 5859619 | LUU187HV | LCN187HV | 10.1 | 20 | 15 | Yes | Ductless | Single-zone | 9300 | 20000 | 22000 | 0.74 | 1.5 | 1.78 | 3.7 | 3.9 | 3.6 | 6820 | 12500 | 14330 | 0.69 | 1.27 | 1.54 | 2.9 | 2.9 | 2.7 | 4550 | 11271 | 0.55 | 1.47 | 2.4 | 2.2 | 51.23% | 78.65% | N/A |  |  | N/A |  | z
LG |  | 6236101 | LSU240HSV3 | LSN240HSV3 | 10.2 | 20 | 12.5 | Yes | Ductless | Single-zone | 3070 | 27600 | 38900 | 0.3 | 2.38 | 4.1 | 3 | 3.4 | 2.8 | 2250 | 16940 | 28020 | 0.26 | 1.92 | 3.42 | 2.6 | 2.6 | 2.4 | 1500 | 24220 | 0.2 | 3.36 | 2.2 | 2.1 | 62.26% | 86.44% | N/A |  |  | N/A |  | z
LG |  | 7184507 | LMU24CHV | Mixed | 10.2 | 19.6 | 12.5 | Yes | Ductless | Multi-zone | 10230 | 23250 | 27900 | 1.171 | 1.859 | 2.6 | 2.6 | 3.7 | 3.1 | 6270 | 14250 | 20394 | 1.008 | 1.61 | 1.76 | 1.8 | 2.6 | 3.4 | 4932 | 14109 | 0.973 | 1.7 | 1.5 | 2.4 | 50.57% | 69.18% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7180062 | LMU24CHV | Non-Ducted Indoor Units | 10.6 | 21.7 | 13.5 | Yes | Ductless | Multi-zone | 9240 | 24000 | 28800 | 1.092 | 1.8 | 2.52 | 2.5 | 3.9 | 3.3 | 5580 | 14500 | 21097 | 0.945 | 1.56 | 1.71 | 1.7 | 2.7 | 3.6 | 4332 | 14595 | 0.917 | 1.65 | 1.4 | 2.6 | 50.68% | 69.18% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7484109 | LSU090HSV4 | LAN090HSV4 | 10.8 | 21.5 | 13.3 | Yes | Ductless | Single-zone | 1023 | 10800 | 17061 | 0.075 | 0.7 | 1.43 | 4 | 4.5 | 3.5 | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.5 | 3.2 | 500 | 9570 | 0.05 | 1 | 2.9 | 2.8 | 56.09% | 86.37% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7484110 | LSU090HSV4 | LSN090HSV4 | 10.8 | 21.5 | 13.3 | Yes | Ductless | Single-zone | 1023 | 10800 | 17061 | 0.07 | 0.7 | 1.35 | 4.3 | 4.5 | 3.7 | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.5 | 3.2 | 500 | 9570 | 0.05 | 1 | 2.9 | 2.8 | 56.09% | 86.37% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7484111 | LSU120HSV4 | LAN120HSV4 | 11 | 21.5 | 12.5 | Yes | Ductless | Single-zone | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3 | 2.7 | 500 | 11670 | 0.054 | 1.41 | 2.7 | 2.4 | 52.62% | 86.44% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7484112 | LSU120HSV4 | LSN120HSV4 | 11 | 21.5 | 12.5 | Yes | Ductless | Single-zone | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3 | 2.7 | 500 | 11670 | 0.054 | 1.41 | 2.7 | 2.4 | 52.62% | 86.44% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7012586 | LSU240HLV | LSN240HLV | 11 | 21.5 | 12.5 | Yes | Ductless | Single-zone | 3070 | 27000 | 38898 | 0.3 | 2.38 | 4.1 | 3 | 3.3 | 2.8 | 2250 | 16570 | 27410 | 0.26 | 1.92 | 3.42 | 2.5 | 2.5 | 2.3 | 1500 | 23690 | 0.2 | 3.36 | 2.2 | 2.1 | 60.9% | 86.43% | N/A |  |  | N/A |  | z
LG |  | 7947563 | LAU090HYV1 | LAN090HYV1 | 12 | 27.5 | 15.65 | Yes | Ductless | Single-zone | 1023 | 11000 | 20472 | 0.07 | 0.71 | 1.32 | 4.3 | 4.5 | 4.5 | 597 | 6750 | 11940 | 0.06 | 0.57 | 1.16 | 2.9 | 3.5 | 3 | 561 | 11220 | 0.06 | 1.14 | 2.7 | 2.9 | 54.81% | 93.97% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG |  | 7849625 | LAU120HYV1 | LAN120HYV1 | 12 | 25.5 | 13.8 | Yes | Ductless | Single-zone | 1023 | 12000 | 22178 | 0.06 | 0.75 | 1.39 | 5 | 4.7 | 4.7 | 676 | 7360 | 14650 | 0.07 | 0.61 | 1.5 | 2.8 | 3.5 | 2.9 | 633 | 13720 | 0.07 | 1.47 | 2.7 | 2.7 | 61.86% | 93.65% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Mitsubishi |  | 7451969 | MXZ-3C24NAHZ | Non-Ducted Indoor Units | 10 | 19 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.83 | 2.53 | 2.06 | 12500 | 25000 | 1.6 | 3.82 | 2.29 | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 22050 | 1.4 | 3.52 | 2.09 | 1.83
Mitsubishi |  | 8996108 | MXZ-3C24NAHZ2 | Non-Ducted Indoor Units | 10 | 19 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.83 | 2.53 | 2.06 | 12500 | 25000 | 1.6 | 3.82 | 2.29 | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 22050 | 1.4 | 3.52 | 2.09 | 1.83
Mitsubishi |  | 4908219 | MUZ-FE09NA | MSZ-FE09NA | 10 | 26 | 15.5 | Yes | Ductless | Single-zone | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.06 | 4.5 | 2.34 | 1700 | 6700 | 12500 | 0.11 | 0.65 | 1.73 | 4.53 | 3.02 | 2.12 | 1200 | 10900 | 0.08 | 1.46 | 4.4 | 2.19 | 60.56% | 87.2% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z
Mitsubishi |  | 4217888 | MUZ-FE18NA | MSZ-FE18NA | 10.3 | 20.2 | 14.2 | Yes | Ductless | Single-zone | 7500 | 21600 | 29700 | 0.52 | 1.54 | 2.42 | 4.23 | 4.11 | 3.6 | 4300 | 11700 | 25850 | 0.37 | 1.24 | 3.28 | 3.41 | 2.76 | 2.31 | 3000 | 21830 | 0.28 | 3.15 | 3.14 | 2.03 | 73.5% | 84.45% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z
Mitsubishi |  | 4934170 | MUZ-FE12NA | MSZ-FE12NA | 10.5 | 23 | 12.9 | Yes | Ductless | Single-zone | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.06 | 4.2 | 2.74 | 1700 | 8300 | 13600 | 0.11 | 0.8 | 1.78 | 4.53 | 3.04 | 2.24 | 1200 | 13600 | 0.08 | 1.62 | 4.4 | 2.46 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z
Mitsubishi |  | 7434486 | MXZ-4C36NAHZ | Mixed | 10.7 | 17.5 | 12.7 | Yes | Ductless | Multi-zone | 22500 | 45000 | 45000 | 1.3 | 3.8 | 3.8 | 5.07 | 3.48 | 3.48 | 22500 | 35000 | 45000 | 2.15 | 4.05 | 5.35 | 3.07 | 2.54 | 2.47 | 22500 | 45000 | 2.62 | 6.21 | 2.52 | 2.16 | 100% | 100% | N/A |  |  | -13 | 22500 | z | 33800 | 3.14 | 5.32 | 2.1 | 1.89
Mitsubishi |  | 7451794 | MXZ-3C30NAHZ | Non-Ducted Indoor Units | 11 | 18 | 12.5 | Yes | Ductless | Multi-zone | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.83 | 2.65 | 2 | 12500 | 28600 | 1.6 | 4.79 | 2.29 | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 25225 | 1.4 | 4.49 | 2.09 | 1.64
Mitsubishi |  | 8993522 | MXZ-3C30NAHZ2 | Non-Ducted Indoor Units | 11 | 18 | 12.5 | Yes | Ductless | Multi-zone | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.83 | 2.65 | 2 | 12500 | 28600 | 1.6 | 4.79 | 2.29 | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 25225 | 1.4 | 4.49 | 2.09 | 1.64
Mitsubishi |  | 7434477 | MXZ-5C42NAHZ | Non-Ducted Indoor Units | 11 | 19 | 13.4 | Yes | Ductless | Multi-zone | 24000 | 48000 | 48000 | 1.17 | 3.43 | 3.43 | 6.01 | 4.1 | 4.1 | 24000 | 35800 | 48000 | 1.66 | 3.65 | 4.87 | 4.23 | 2.87 | 2.89 | 24000 | 48000 | 1.91 | 5.61 | 3.69 | 2.51 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 24000 | z | 36000 | 2.5 | 4.8 | 2.81 | 2.2
Mitsubishi |  | 8635969 | PUZ-HA36NHA5 | PVA-A36AA4 | 11 | 17.8 | 12.5 | Yes | Ducted | N/A | 18000 | 38000 | 40000 | 1.14 | 3.04 | 3.36 | 4.63 | 3.66 | 3.49 | 19000 | 25000 | 38000 | 2.03 | 3.33 | 5.4 | 2.74 | 2.2 | 2.06 | 15000 | 38000 | 1.73 | 6.1 | 2.54 | 1.82 | 95% | 100% | N/A |  |  | -13 | 13000 | z | 29000 | 1.77 | 6.15 | 2.15 | 1.38
Mitsubishi |  | 7434482 | MXZ-4C36NAHZ | Non-Ducted Indoor Units | 11.3 | 19.1 | 14 | Yes | Ductless | Multi-zone | 22500 | 45000 | 45000 | 1.09 | 3.34 | 3.34 | 6.05 | 3.95 | 3.95 | 22500 | 34000 | 45000 | 1.55 | 3.5 | 4.74 | 4.26 | 2.85 | 2.78 | 22500 | 45000 | 1.78 | 5.46 | 3.71 | 2.41 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 22500 | z | 33800 | 2.33 | 4.68 | 2.83 | 2.12
Mitsubishi |  | 8854559 | MUFZ-KJ18NAHZ | MFZ-KJ18NA | 11.3 | 21 | 12.6 | Yes | Ductless | Single-zone | 5700 | 21000 | 29000 | 0.48 | 1.73 | 3.43 | 3.48 | 3.56 | 2.48 | 3250 | 12800 | 23000 | 0.35 | 1.43 | 3.21 | 2.72 | 2.62 | 2.1 | 2260 | 21000 | 0.26 | 3 | 2.55 | 2.05 | 72.41% | 91.3% | Integrated | 98W @208V; 120W @ 230 V |  | -13 | 840 | z | 15700 | 0.13 | 2.3 | 1.89 | 2
Mitsubishi |  | 8854558 | MUFZ-KJ15NAHZ | MFZ-KJ15NA | 11.6 | 21.8 | 13.5 | Yes | Ductless | Single-zone | 5700 | 18000 | 25000 | 0.48 | 1.41 | 3.41 | 3.48 | 3.74 | 2.15 | 3250 | 12000 | 20500 | 0.35 | 1.3 | 3.19 | 2.72 | 2.71 | 1.88 | 2260 | 18000 | 0.26 | 2.95 | 2.55 | 1.79 | 72% | 87.8% | Integrated | 98W @208V; 120W @ 230 V |  | -13 | 840 | z | 14000 | 0.13 | 2.28 | 1.89 | 1.8
Mitsubishi |  | 7002444 | MUZ-FH15NA | MSZ-FH15NA | 12 | 22 | 12.5 | Yes | Ductless | Single-zone | 5150 | 18000 | 24000 | 0.43 | 1.3 | 3.36 | 3.51 | 4.06 | 2.09 | 2950 | 11000 | 18000 | 0.31 | 1.02 | 2.48 | 2.79 | 3.16 | 2.13 | 2050 | 18000 | 0.23 | 2.95 | 2.61 | 1.79 | 75% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 | z | 14600 | 0.11 | 2.35 | 2 | 1.82
Mitsubishi |  | 8797133 | MUZ-FH18NA2 | MSZ-FH18NA2 | 12 | 21 | 12.5 | Yes | Ductless | Single-zone | 5150 | 20300 | 30000 | 0.43 | 1.72 | 3.39 | 3.51 | 3.46 | 2.59 | 2950 | 13700 | 20300 | 0.31 | 1.32 | 2.8 | 2.79 | 3.04 | 2.12 | 2050 | 20300 | 0.23 | 2.96 | 2.61 | 2.01 | 67.67% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 | z | 14000 | 0.11 | 2.35 | 2 | 1.74
Mitsubishi |  | 8849446 | MUFZ-KJ12NAHZ | MFZ-KJ12NA | 12 | 25.5 | 13.6 | Yes | Ductless | Single-zone | 2900 | 13000 | 22800 | 0.27 | 0.9 | 2.39 | 3.15 | 4.23 | 2.8 | 1650 | 8800 | 14800 | 0.2 | 0.93 | 1.89 | 2.42 | 2.77 | 2.29 | 1150 | 13000 | 0.15 | 1.81 | 2.25 | 2.1 | 57.02% | 87.84% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 | z | 8000 | 0.07 | 1.28 | 1.76 | 1.83
Mitsubishi |  | 7002063 | MUZ-FH12NA | MSZ-FH12NA | 12.5 | 26.1 | 13.8 | Yes | Ductless | Single-zone | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.87 | 4.2 | 2.68 | 2100 | 8000 | 13600 | 0.2 | 0.72 | 1.9 | 3.08 | 3.26 | 2.1 | 1450 | 13600 | 0.15 | 1.8 | 2.83 | 2.21 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 550 | z | 9900 | 0.07 | 1.6 | 2.3 | 1.81
Mitsubishi |  | 8854557 | MUFZ-KJ09NAHZ | MFZ-KJ09NA | 13 | 28.2 | 15.8 | Yes | Ductless | Single-zone | 2900 | 11000 | 19000 | 0.27 | 0.75 | 2.37 | 3.15 | 4.3 | 2.35 | 1650 | 7500 | 13400 | 0.2 | 0.8 | 1.86 | 2.42 | 2.75 | 2.11 | 1150 | 11000 | 0.15 | 1.6 | 2.25 | 2.01 | 57.89% | 82.09% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 | z | 7000 | 0.07 | 1.27 | 1.76 | 1.62
Mitsubishi |  | 7002062 | MUZ-FH09NA | MSZ-FH09NA | 13.5 | 30.5 | 16.1 | Yes | Ductless | Single-zone | 1600 | 10900 | 18000 | 0.11 | 0.71 | 1.47 | 4.26 | 4.5 | 3.59 | 920 | 6700 | 12200 | 0.08 | 0.6 | 1.44 | 3.37 | 3.27 | 2.48 | 640 | 10900 | 0.06 | 1.35 | 3.13 | 2.32 | 60.56% | 89.34% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 | z | 7300 | 0.03 | 1.25 | 2.34 | 1.71
Mitsubishi |  | 8797130 | MUZ-FH06NA | MSZ-FH06NA | 13.5 | 33.1 | 19 | Yes | Ductless | Single-zone | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 | 920 | 5900 | 10700 | 0.08 | 0.5 | 1 | 3.37 | 3.46 | 3.13 | 640 | 8700 | 0.06 | 0.91 | 3.13 | 2.8 | 62.14% | 81.31% | Accessory (MAC-640BH-U) | 106W @208V; 130W @230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 | z | 6400 | 0.03 | 0.8 | 2.34 | 2.34
Nortek Global | Maytag | 5597453 | PSH4BG024K | B6VMAX024K-B | 10 | 19 | 13.9 | Yes | Ducted | N/A | 10200 | 22400 | 24700 | 0.7 | 1.7 | 2.2 | 4.2705 | 3.8616 | 3.2904 | 6100 | 14200 | 15800 | 0.7 | 1.5 | 1.9 | 2.5539 | 2.7744 | 2.4371 | 4700 | 12600 | 0.6 | 1.8 | 2.2957 | 2.0515 | 51.01% | 79.75% | N/A |  |  | N/A |  | z
Nortek Global | Maytag | 5597457 | PSH4BG036K | B6VMAX036K-B | 10 | 19 | 12.9 | Yes | Ducted | N/A | 16500 | 34400 | 36800 | 1 | 2.7 | 3.2 | 4.8357 | 3.7339 | 3.3703 | 9900 | 21800 | 23900 | 1 | 2.4 | 2.7 | 2.9014 | 2.6621 | 2.5942 | 7500 | 20100 | 0.9 | 2.6 | 2.4423 | 2.2657 | 54.62% | 84.1% | N/A |  |  | N/A |  | z
Panasonic | Panasonic | 7958200 | CS-E18RKUA | CU-E18RKUAW | 10 | 19.5 | 13.2 | Yes | Ductless | Singlezone | 5800 | 21600 | 22000 | 0.38 | 1.75 | 1.8 | 4.47 | 3.62 | 3.57 | 3400 | 11600 | 12000 | 0.34 | 1.3 | 1.35 | 2.9326 | 2.6167 | 2.6 | 2600 | 10100 | 0.3 | 1.32 | 2.5415 | 2.2438 | 45.91% | 84.17% | N/A |  |  | -5°F | 1900 |  | 8200 | 0.26 | 1.29 | 2.143 | 1.8641
Panasonic | Panasonic | 9125308 | CU-E9SD3UA | CS-E9SD3UAW | 10 | 20.5 | 13 | Yes | Ductless | Singlezone | 4100 | 9000 | 10200 | 0.25 | 0.69 | 0.85 | 4.8 | 3.82 | 3.53 | 3200 | 7900 | 9000 | 0.23 | 0.91 | 1.12 | 4.0801 | 2.5458 | 2.36 | 2400 | 7800 | 0.2 | 1.11 | 3.5191 | 2.0607 | 76.47% | 86.67% | N/A |  |  | -5°F | 1600 |  | 6700 | 0.16 | 1.1 | 2.9326 | 1.7862
Panasonic | Panasonic | 9125309 | CU-E12SD3UA | CS-E12SD3UAW | 10 | 20 | 12.5 | Yes | Ductless | Singlezone | 4100 | 11500 | 13300 | 0.25 | 0.92 | 1.15 | 4.8 | 3.64 | 3.39 | 3200 | 9500 | 11000 | 0.23 | 1.15 | 1.44 | 4.0801 | 2.4225 | 2.24 | 2400 | 9600 | 0.2 | 1.52 | 3.5191 | 1.8521 | 72.18% | 87.27% | N/A |  |  | -5°F | 1600 |  | 8200 | 0.16 | 1.6 | 2.9326 | 1.5029
Panasonic | Panasonic | 7958198 | CS-E9RKUA | CU-E9RKUAW | 11 | 23 | 13 | Yes | Ductless | Singlezone | 4100 | 12000 | 14100 | 0.2 | 1.12 | 1.5 | 6 | 3.14 | 2.76 | 3200 | 8100 | 9500 | 0.19 | 0.99 | 1.33 | 4.939 | 2.3994 | 2.1 | 2400 | 8300 | 0.16 | 1.32 | 4.3988 | 1.844 | 58.87% | 87.37% | N/A |  |  | -5°F | 1600 |  | 7000 | 0.13 | 1.31 | 3.6093 | 1.567
Panasonic | Panasonic | 7958199 | CS-E12RKUA | CU-E12RKUAW | 11 | 22.5 | 12.5 | Yes | Ductless | Singlezone | 4100 | 13800 | 16300 | 0.2 | 1.25 | 1.71 | 6 | 3.24 | 2.79 | 3200 | 8900 | 10500 | 0.19 | 1.05 | 1.44 | 4.939 | 2.4857 | 2.14 | 2400 | 9100 | 0.16 | 1.51 | 4.3988 | 1.7673 | 55.83% | 86.67% | N/A |  |  | -5°F | 1600 |  | 7900 | 0.13 | 1.6 | 3.6093 | 1.4479
Panasonic | Panasonic | 9571162 | CU-XE15SKUA | CS-XE15SKUA | 12 | 22.1 | 12.5 | Yes | Ductless | Singlezone | 3300 | 18000 | 24000 | 0.2 | 1.3 | 2.65 | 4.9 | 4.06 | 2.65 | 2000 | 11000 | 16500 | 0.16 | 1.02 | 2.3 | 3.6657 | 3.16 | 2.1 | 1500 | 15700 | 0.15 | 2.32 | 2.9326 | 1.98 | 65.42% | 95.15% | included with outdoor unit (Replacement part # CWA341072) | 100 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1100 |  | 14900 | 0.13 | 2.34 | 2.4814 | 1.8673
Panasonic | Panasonic | 8861565 | CU-XE12SKUA | CS-XE12SKUA | 12.5 | 26.2 | 14.7 | Yes | Ductless | Singlezone | 3000 | 13600 | 23000 | 0.15 | 0.95 | 2.1 | 5.93 | 4.1955 | 3.2 | 2100 | 10400 | 12500 | 0.14 | 1.05 | 1.6662 | 4.3988 | 2.9028 | 2.2 | 1700 | 12500 | 0.12 | 1.99 | 4.1544 | 1.84 | 54.35% | 100% | included with outdoor unit CU-XE12SKUA | 780 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 11800 | 0.1 | 2.01 | 3.8123 | 1.7216
Panasonic | Panasonic | 8860533 | CU-XE9SKUA | CS-XE9SKUA | 14 | 30.6 | 17.05 | Yes | Ductless | Singlezone | 3000 | 10900 | 18000 | 0.15 | 0.67 | 1.65 | 5.93 | 4.78 | 3.21 | 2100 | 8000 | 11000 | 0.14 | 0.75 | 1.38 | 4.3988 | 3.1261 | 2.34 | 1700 | 11000 | 0.12 | 1.73 | 4.1544 | 1.86 | 61.11% | 100% | included with outdoor unit CU-XE9SKUA | 510 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 10400 | 0.1 | 1.72 | 3.8123 | 1.7732
Toshiba Carrier | Carrier | 6960758 | RAS-09EAV-UL | RAS-09EKV-UL | 10 | 20 | 13 | Yes | Ductless | Single-zone | 3070 | 10800 | 16350 | 0.17 | 0.8 | 1.4 | 5.29 | 3.95 | 3.42 | 1795 | 6313 | 9551 | 0.127 | 0.61 | 1.042 | 4.14 | 3.03 | 2.69 | 1224 | 6519 | 0.109 | 0.895 | 3.29 | 2.13 | 39.87% | 68.25% | N/A |  |  | -4 | 828 | z | 4409 | 0.096 | 0.787 | 2.52 | 1.64
Toshiba Carrier | Carrier | 6960762 | RAS-15EAV-UL | RAS-15EKV-UL | 10 | 20 | 13 | Yes | Ductless | Single-zone | 2750 | 18000 | 21500 | 0.143 | 1.4 | 1.9 | 5.64 | 3.77 | 3.32 | 1608 | 10400 | 12553 | 0.106 | 1.042 | 1.415 | 4.444 | 2.93 | 2.6 | 1096 | 8752 | 0.091 | 1.215 | 3.52 | 2.11 | 40.71% | 69.72% | N/A |  |  | -4 | 742 | z | 5798 | 0.08 | 1.067 | 2.72 | 1.59
Toshiba Carrier | Carrier | 6960764 | RAS-17EAV-UL | RAS-17EKV-UL | 10 | 19 | 12.6 | Yes | Ductless | Single-zone | 2750 | 20200 | 21500 | 0.15 | 1.63 | 1.91 | 5.37 | 3.63 | 3.3 | 1608 | 10500 | 12553 | 0.112 | 1.214 | 1.422 | 4.2 | 2.53 | 2.59 | 1096 | 8572 | 0.096 | 1.221 | 3.35 | 2.06 | 39.87% | 68.29% | N/A |  |  | -4 | 742 | z | 5798 | 0.084 | 1.073 | 2.59 | 1.58
Trane |  | 7151531 | 4TXK2709A10N0AA | 4MXW2709A10N0AA | 10 | 27 | 14.5 | Yes | Ductless | Singlezone | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 | 1480 | 8000 | 0.15 | 1.095 | 2.8916 | 2.1412 | 72.73% | 75.25% | Integrated | 72W | Heater on below 34°F | N/A |  | z
Trane |  | 7151533 | 4TXK2712A10NAA | 4MXW2712A10N0AA | 10 | 25 | 13 | Yes | Ductless | Singlezone | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 | 2100 | 8300 | 0.085 | 1.131 | 7.2406 | 2.1507 | 59.29% | 95.4% | Integrated | 72W | Heater on below 34°F | N/A
Trane |  | 7151535 | 4TXK2718A10N0AA | 4MXW2718A10N0AA | 10 | 21 | 12.5 | Yes | Ductless | Singlezone | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 | 2388 | 15400 | 0.42 | 2.29 | 1.6663 | 1.9709 | 66.37% | 78.28% | Integrated | 160W | Heater on below 34°F | N/A
Trane |  | 6749942 | 4TWV0024A1 | *AM8C0B30V21 | 10 | 19.25 | 13.75 | Yes | Ducted | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 | 11176 | 13000 | 1.58 | 1.84 | 2.08 | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A
Trane |  | 6992578 | 4TWV0036A1 | *AM8C0B30V21 | 10 | 20 | 13 | Yes | Ducted | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 | 16688 | 20160 | 2.64 | 3.16 | 1.86 | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A
Trane |  | 7599437 | 4TWV0036A1 | *AM8C0C48V41 | 10 | 20.75 | 13.5 | Yes | Ducted | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 | 16548 | 19800 | 2.54 | 3 | 1.9 | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A
Trane |  | 7125586 | 4TWV0036A1 | *UHMB060ACV3 4TXCB004CC3 | 10 | 18.5 | 12.5 | Yes | Ducted | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 | 16934 | 20300 | 2.82 | 3.36 | 1.76 | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A
Trane |  | 6796600 | 4TWV0036A1 | *UD2C080ACV4 4TXCC007CC3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 | 16488 | 19800 | 2.7 | 3.22 | 1.78 | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A
Trane |  | 6796602 | 4TWV0036A1 | *UD2C100ACV5 4TXCC007CC3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 | 16588 | 19900 | 2.7 | 3.2 | 1.8 | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A
Trane |  | 7125588 | 4TWV0036A1 | *DHMB060BCV3 4TXFH036CZ3 | 10 | 19.5 | 12.5 | Yes | Ducted | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 | 17034 | 20340 | 2.78 | 3.28 | 1.8 | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A
Trane |  | 6796604 | 4TWV0036A1 | *UD2C080ACV4 4TXFH036CZ3 | 10 | 20 | 13 | Yes | Ducted | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 | 16628 | 19900 | 2.66 | 3.16 | 1.84 | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A
Trane |  | 7125587 | 4TWV0036A1 | *UHMB060ACV3 4TXFH036CZ3 | 10 | 18.75 | 12.5 | Yes | Ducted | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 | 16788 | 20040 | 2.78 | 3.32 | 1.76 | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A
Trane |  | 6749944 | 4TWV0048A1 | *AM8C0C48V41 | 10 | 19.25 | 12.5 | Yes | Ducted | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 | 22446 | 26720 | 3.72 | 4.44 | 1.76 | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A
Trane |  | 7161152 | 4TWV0048A1 | *AM8C0C60V51 | 10 | 19.25 | 12.5 | Yes | Ducted | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 | 22486 | 26780 | 3.64 | 4.34 | 1.8 | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A
Trane |  | 6750459 | 4TWV8024A1 | *AM8C0B30V21 | 10 | 18 | 13 | Yes | Ducted | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 | 11176 | 13000 | 1.58 | 1.84 | 2.08 | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A
Trane |  | 6750234 | 4TWV8036A1 | *AM8C0C36V31 | 10 | 18 | 13 | Yes | Ducted | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 | 16488 | 19680 | 2.66 | 3.18 | 1.82 | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A
Trane |  | 7035765 | 4TWV8036A1 | *DD2C100ACV5 4NXCC005AS3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 | 16828 | 20200 | 2.7 | 3.26 | 1.82 | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A
Trane |  | 6796635 | 4TWV8037A1 | *AM8C0B30V21 | 10 | 18 | 13 | Yes | Ducted | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 | 16688 | 20160 | 2.66 | 3.16 | 1.84 | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A
Trane |  | 6796636 | 4TWV8037A1 | *UD2B080ACV3 4TXCB004CC3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 | 16934 | 20240 | 2.8 | 3.32 | 1.78 | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A
Trane |  | 6796638 | 4TWV8037A1 | *UD2C080ACV4 4TXCC007CC3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 | 16488 | 19800 | 2.7 | 3.22 | 1.78 | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A
Trane |  | 6796639 | 4TWV8037A1 | *UD2C100ACV5 4TXCC007CC3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 | 16588 | 19900 | 2.7 | 3.2 | 1.8 | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A
Trane |  | 7125597 | 4TWV8037A1 | *DHMB060BCV3 4TXFH036CZ3 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 | 17034 | 20340 | 2.78 | 3.28 | 1.8 | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A
Trane |  | 6796641 | 4TWV8037A1 | *UD2C080ACV4 4TXFH036CZ3 | 10 | 18 | 13 | Yes | Ducted | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 | 16628 | 19900 | 2.66 | 3.16 | 1.84 | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A
Trane |  | 6750235 | 4TWV8048A1 | *AM8C0C48V41 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 | 22792 | 27080 | 3.66 | 4.38 | 1.82 | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A |  | z
Trane |  | 6750461 | 4TWV8049A1 | *AM8C0C48V41 | 10 | 18 | 12.5 | Yes | Ducted | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 | 22446 | 26720 | 3.72 | 4.44 | 1.76 | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z
Trane | Trane | 9150125 | 4TXK3818A10NUAA | 4MXW3818A10NUAA | 12 | 24.5 | 13.5 | Yes | Ductless | Singlezone | 3700 | 18000 | 24400 | 0.35 | 1.5 | 2.5 | 3.0982 | 3.5169 | 2.8604 | 3070 | 14200 | 23100 | 0.36 | 1.455 | 3.25 | 2.4992 | 2.8602 | 2.0831 | 2388 | 19110 | 0.37 | 2.98 | 1.8915 | 1.8794 | 78.32% | 82.73% | Integrated | 160W | Heater on below 34°F | N/A |  | z
Trane | Trane | 9150127 | 4TXK3824A10NUAA | 4MXW3824A10NUAA | 12 | 21.5 | 13 | Yes | Ductless | Singlezone | 6800 | 24000 | 32400 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5664 | 3396 | 15500 | 26263 | 0.344 | 1.57 | 3.381 | 2.8932 | 2.8934 | 2.2765 | 2887 | 22553 | 0.33 | 3.2 | 2.5639 | 2.0655 | 69.61% | 85.87% | Integrated | 160W | Heater on below 34°F | N/A |  | z
Trane | Trane | 9150123 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | 14 | 30.5 | 15.3 | Yes | Ductless | Singlezone | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 | 2600 | 8000 | 0.22 | 0.86 | 3.4636 | 2.7262 | 42.78% | 88.89% | Integrated | 72W | Heater on below 34°F | N/A |  | z
Trane | Trane | 9150121 | 4TXK3809A10NUAA | 4MXW3809A10NUAA | 15 | 38 | 16.5 | Yes | Ductless | Singlezone | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 | 1745 | 12976.6 | 0.28 | 1.8216 | 1.8265 | 2.0878 | 95.42% | 88.82% | Integrated | 72W | Heater on below 34°F | N/A |  | z

## Delisted (on 1.1.17)
Manufacturer | Brand (if applicable) | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | HSPF (Region IV): | SEER | EER (@ 95°F) | ENERGY STAR Certified | Ductless or Ducted | If Ductless, Multi-zone or Single-zone? | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Minimum Input Power 47°F | Rated Input Power 47°F | Maximum Input Power 47°F | Minimum COP 47°F | Rated COP 47°F | Maximum COP 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Minimum Input Power 17°F | Rated Input Power 17°F | Maximum Input Power 17°F | Minimum COP 17°F | Rated COP 17°F | Maximum COP 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Minimum Input Power 5°F | Maximum Input Power 5°F | Minimum COP 5°F | Maximum COP 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Minimum Input Power X°F | Maximum Input Power X°F | Minimum COP X°F | Maximum COP X°F
LG |  | 7180060 | LMU18CHV | Non-Ducted Indoor Units | 9.7 | 22 | 13 | Yes | Ductless | Multi-zone | 10248 | 22000 | 24000 | 1.155 | 2.04 | 2.42 | 2.6 | 3.2 | 2.9 | 6288 | 13500 | 19161 | 0.924 | 1.63 | 2.03 | 2 | 2.4 | 2.8 | 4950 | 14807 | 0.861 | 1.86 | 1.7 | 2.3 | 61.7% | 77.28% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Carrier | Bryant | 9854623 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 9854622 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Lennox Industries, Inc. | Lennox | 8994419 | MLA018S4M-1P | non-ducted indoor units | 9.8 | 21.5 | 12.5 | Yes | Ductless | Multizone | 6020 | 20000 | 28500 | 0.715 | 1.72 | 2.7 | 2.4675 | 3.4078 | 3.0935 | 5743 | 12600 | 26457 | 0.804 | 1.388 | 3.978 | 2.0934 | 2.6604 | 1.9492 | 5516 | 24120 | 0.832 | 3.892 | 1.943 | 1.8163 | 84.63% | 91.17% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Mitsubishi |  | 7451974 | MXZ-2C20NAHZ | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98
Mitsubishi |  | 8996530 | MXZ-2C20NAHZ2 | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98