## Current Product List- Jan 2018
General Information
DISCLAIMER- Some of the performance values reported as part of the Cold-Climate ASHP Specification are NOT derived from industry standard test procedures or third-party tested/verified (i.e. performance values at 5°F). Performance in some instances may be represented by manufacturer’s engineering data.
See column BL (furtherest to the right) for the date products were added to the list starting in 2018
Products in grey are the ones not found in the AHRI database as of June 12, 2017.
[15 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP | [8 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  | COP
Updated: March 16, 2018
Manufacturer | Brand (if applicable) | Model Name | AHRI Certificate No. | AHRI Type | Outdoor Unit Model | Indoor Unit Model(s) | Cooling Capacity (Btuh) | EER (@ 95°F) | SEER | HSPF (Region IV): | ENERGY STAR Certified | Centrally Ducted or Ductless | If Ductless, Multi-zone or Single-zone? | Ductless Indoor Type | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F |  | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F |  | Minimum Capacity 5°F |  | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F |  | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F |  | COP at Max. Capacity 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F | COP at Max. Capacity X°F | Date added to List
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208521 | HRCU-A-CB-O | RXG09HVJU | FTXG09HVJU | 9000 | 15.8 | 26.1 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 12000 | 18670 | 0.224 | 0.78 | 1.94 | 6.11 | 4.51 | 2.82 |  | 3003 | 8100 | 12170 | 0.194 | 0.72 | 1.68 | 4.54 | 3.3 | 2.12 |  | 2330 |  | 9460 | 0.182 |  | 1.57 | 3.75 |  | 1.77 | 50.67% | 77.73% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7430 |  | 1.49 |  | 1.46
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208522 | HRCU-A-CB-O | RXG12HVJU | FTXG12HVJU | 12000 | 14 | 24.2 | 10.55 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 16000 | 19130 | 0.224 | 1.16 | 2.14 | 6.11 | 4.04 | 2.62 |  | 3003 | 10400 | 12920 | 0.192 | 0.98 | 1.78 | 4.58 | 3.1 | 2.13 |  | 2330 |  | 10040 | 0.181 |  | 1.67 | 3.77 |  | 1.76 | 52.48% | 77.71% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7880 |  | 1.58 |  | 1.46
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208523 | HRCU-A-CB-O | RXG15HVJU | FTXG15HVJU | 15000 | 12.9 | 21 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 18000 | 21280 | 0.234 | 1.32 | 2.16 | 5.85 | 3.99 | 2.89 |  | 3003 | 11100 | 14340 | 0.203 | 1.08 | 1.87 | 4.34 | 3 | 2.25 |  | 2330 |  | 11150 | 0.19 |  | 1.75 | 3.59 |  | 1.87 | 52.4% | 77.75% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 8750 |  | 1.67 |  | 1.54
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837467 | HRCU-A-CB | SUZ-KA12NA | SEZ-KD12NA | 11500 | 12.5 | 16 | 10 | Yes | Ductless | Single-zone | Ducted Indoor Units | 4800 | 13600 | 16400 | 0.34 | 1.14 | 1.52 | 4.1375 | 3.4963 | 3.1621 |  | 3100 | 9000 | 10800 | 0.36 | 0.92 | 1.2 | 2.5237 | 2.867 | 2.6376 |  | 2199 |  | 7400 | 0.27 |  | 0.9 | 2.3869 |  | 2.4097 | 45.12% | 75% | N/A |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837470 | HRCU-A-CB | SUZ-KA18NA | SEZ-KD18NA | 17200 | 12.5 | 17.5 | 10 | Yes | Ductless | Single-zone | Ducted Indoor Units | 4800 | 21600 | 24900 | 0.26 | 1.7 | 2.15 | 5.4105 | 3.7237 | 3.3942 |  | 2900 | 13100 | 15000 | 0.31 | 1.35 | 1.8 | 2.7416 | 2.8439 | 2.4423 |  | 1900 |  | 9900 | 0.23 |  | 1.32 | 2.421 |  | 2.198 | 39.76% | 74.19% | N/A |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4217888 | N/A | MUZ-FE18NA | MSZ-FE18NA | 18000 | 14.2 | 20.2 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 7500 | 21600 | 29700 | 0.52 | 1.54 | 2.42 | 4.23 | 4.11 | 3.6 |  | 4300 | 11700 | 25850 | 0.37 | 1.24 | 3.28 | 3.41 | 2.76 | 2.31 |  | 3000 |  | 21830 | 0.28 |  | 3.15 | 3.14 |  | 2.03 | 73.5% | 84.45% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4908219 | HRCU-A-CB-O | MUZ-FE09NA | MSZ-FE09NA | 9000 | 15.5 | 26 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8617 | 4.5 | 2.34 |  | 1700 | 6700 | 12500 | 0.11 | 0.65 | 1.73 | 4.53 | 3.02 | 2.12 |  | 1200 |  | 10900 | 0.08 |  | 1.46 | 4.4 |  | 2.19 | 60.56% | 87.2% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4934170 | HRCU-A-CB-O | MUZ-FE12NA | MSZ-FE12NA | 12000 | 12.9 | 23 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8617 | 4.2 | 2.74 |  | 1700 | 8300 | 13600 | 0.11 | 0.8 | 1.78 | 4.53 | 3.04 | 2.24 |  | 1200 |  | 13600 | 0.08 |  | 1.62 | 4.4 |  | 2.46 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063325 | HRCU-A-CB-O | AOU9RLS2 | ASU9RLS2 | 9000 | 16.1 | 27.2 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.8 | 1.99 | 4.5 | 4.4 | 3.24 |  | 2320 | 9400 | 16400 | 0.2 | 1.09 | 1.97 | 3.4 | 2.54 | 2.45 |  | 2150 |  | 15000 | 0.21 |  | 2.06 | 3 |  | 2.18 | 68.18% | 91.46% | N/A |  |  | -5 | 1945 | z | 13500 | 0.21 | 2.05 | 2.71 | 2
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063326 | HRCU-A-CB-O | AOU12RLS2 | ASU12RLS2 | 12000 | 13.8 | 25 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.2 | 2 | 4.5 | 3.91 | 3.24 |  | 2491 | 10200 | 17900 | 0.2 | 1.1 | 2 | 3.65 | 2.72 | 2.63 |  | 2320 |  | 16500 | 0.21 |  | 2.1 | 3.24 |  | 2.34 | 74.63% | 92.18% | N/A |  |  | -5 | 2081 | z | 15000 | 0.21 | 2.1 | 2.9 | 2.1
Daikin AC (Americas), Inc | Daikin | LV Series | 5265753 | HRCU-A-CB-O | RXS09LVJU | FTXS09LVJU | 9000 | 15.3 | 24.5 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4400 | 12000 | 15600 | 0.22 | 0.79 | 1.27 | 5.99 | 4.45 | 3.6 |  | 2408 | 6520 | 8465 | 0.15 | 0.55 | 0.88 | 4.72 | 3.48 | 2.81 |  | 1982 |  | 6968 | 0.14 |  | 0.84 | 4.08 |  | 2.43 | 44.67% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1727 | z | 6070 | 0.14 | 0.82 | 3.66 | 2.18
Daikin AC (Americas), Inc | Daikin | LV Series | 5265755 | HRCU-A-CB-O | RXS12LVJU | FTXS12LVJU | 12000 | 12.8 | 23 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4800 | 14400 | 18000 | 0.22 | 0.97 | 1.27 | 6.53 | 4.35 | 4.15 |  | 2593 | 7816 | 9780 | 0.15 | 0.67 | 0.88 | 5.08 | 3.4 | 3.25 |  | 2135 |  | 8051 | 0.14 |  | 0.84 | 4.39 |  | 2.81 | 44.73% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1860 | z | 7013 | 0.14 | 0.82 | 3.94 | 2.52
Daikin AC (Americas), Inc | Daikin | LV Series | 5265756 | HRCU-A-CB-O | RXS15LVJU | FTXS15LVJU | 15000 | 14.4 | 20.6 | 11.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 18000 | 22300 | 0.39 | 1.32 | 1.64 | 4.35 | 4 | 3.97 |  | 3149 | 9780 | 12114 | 0.27 | 0.92 | 1.14 | 3.4 | 3.13 | 3.11 |  | 2592 |  | 9972 | 0.26 |  | 1.09 | 2.94 |  | 2.69 | 44.72% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 8687 | 0.25 | 1.06 | 2.64 | 2.41
Daikin AC (Americas), Inc | Daikin | LV Series | 5265757 | HRCU-A-CB-O | RXS18LVJU | FTXS18LVJU | 18000 | 12.7 | 20.3 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 21600 | 26700 | 0.41 | 1.71 | 2.12 | 4.17 | 3.7 | 3.7 |  | 3149 | 11725 | 14485 | 0.28 | 1.19 | 1.47 | 3.26 | 2.89 | 2.89 |  | 2592 |  | 11924 | 0.27 |  | 1.4 | 2.82 |  | 2.49 | 44.66% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 10387 | 0.26 | 1.36 | 2.53 | 2.24
Daikin AC (Americas), Inc | Daikin | LV Series | 5265758 | HRCU-A-CB-O | RXS24LVJU | FTXS24LVJU | 21400 | 12.5 | 20 | 10.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7800 | 25400 | 31400 | 0.54 | 2.21 | 2.75 | 4.25 | 3.37 | 3.34 |  | 4260 | 13781 | 17041 | 0.37 | 1.54 | 1.91 | 3.34 | 2.63 | 2.61 |  | 3507 |  | 14028 | 0.36 |  | 1.82 | 2.89 |  | 2.26 | 44.68% | 82.32% | Accessory (KEH041A43) |  | Temp. below 23 degrees | 0 | 3055 | z | 12220 | 0.35 | 1.77 | 2.59 | 2.03
Nortek Global | Maytag | M1200 | 5597453 | HRCU-A-CB | PSH4BG024K | B6VMAX024K-B | 24600 | 13.9 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 10200 | 22400 | 24700 | 0.7 | 1.7 | 2.2 | 4.2705 | 3.8616 | 3.2904 |  | 6100 | 14200 | 15800 | 0.7 | 1.5 | 1.9 | 2.5539 | 2.7744 | 2.4371 |  | 4700 |  | 12600 | 0.6 |  | 1.8 | 2.2957 |  | 2.0515 | 51.01% | 79.75% | N/A |  |  | N/A
Nortek Global | Maytag | M1200 | 5597457 | HRCU-A-CB | PSH4BG036K | B6VMAX036K-B | 34800 | 12.9 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 16500 | 34400 | 36800 | 1 | 2.7 | 3.2 | 4.8357 | 3.7339 | 3.3703 |  | 9900 | 21800 | 23900 | 1 | 2.4 | 2.7 | 2.9014 | 2.6621 | 2.5942 |  | 7500 |  | 20100 | 0.9 |  | 2.6 | 2.4423 |  | 2.2657 | 54.62% | 84.1% | N/A |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751311 | HRCU-A-CB-O | AOU9RLFC | AUU9RLF | 9000 | 14.5 | 24 | 13 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18000 | 0.15 | 0.89 | 1.8 | 6 | 3.95 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 1.92 | 4.54 | 2.14
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751312 | HRCU-A-CB-O | AOU9RLFC | ARU9RLF | 9000 | 14.5 | 21.5 | 12.2 | Yes | Ductless | Single-zone | Ducted Indoor Unit | 3100 | 12000 | 18000 | 0.15 | 0.85 | 1.8 | 6 | 4.14 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 1.92 | 4.54 | 2.14
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751313 | HRCU-A-CB-O | AOU12RLFC | AUU12RLF | 12000 | 12.8 | 21.9 | 12.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19400 | 0.15 | 1.44 | 2 | 6 | 3.26 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2.32 | 3.75 | 1.9
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751314 | HRCU-A-CB-O | AOU12RLFC | ARU12RLF | 12000 | 12.8 | 20 | 11.5 | Yes | Ductless | Single-zone | Ducted Indoor Unit | 3100 | 16000 | 19400 | 0.15 | 1.3 | 2 | 6 | 3.61 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2.32 | 3.75 | 1.9
LG Electronics USA, Inc | LG |  | 5859619 | HRCU-A-CB-O | LUU187HV | LCN187HV | 18000 | 15 | 20 | 10.1 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 9300 | 20000 | 22000 | 0.74 | 1.5 | 1.78 | 3.7 | 3.9 | 3.6 |  | 6820 | 12500 | 14330 | 0.69 | 1.27 | 1.54 | 2.9 | 2.9 | 2.7 |  | 4550 |  | 11271 | 0.55 |  | 1.47 | 2.4 |  | 2.2 | 51.23% | 78.65% | N/A |  |  | N/A |  | z
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 6233140 | HRCU-A-CB-O | LAU120HYV | LAN120HYV | 12000 | 14.1 | 25.5 | 11.5 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 1023 | 13600 | 22178 | 0.06 | 0.86 | 1.98 | 4.9969 | 4.6346 | 3.2827 |  | 676 | 8350 | 14650 | 0.07 | 0.69 | 1.5 | 2.8302 | 3.5466 | 2.8623 |  | 633 |  | 13720 | 0.07 |  | 1.47 | 2.6502 |  | 2.7353 | 61.86% | 93.65% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
LG Electronics USA, Inc | LG |  | 6236101 | HRCU-A-CB-O | LSU240HSV3 | LSN240HSV3 | 22000 | 12.5 | 20 | 10.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 27600 | 38900 | 0.3 | 2.38 | 4.1 | 3 | 3.4 | 2.8 |  | 2250 | 16940 | 28020 | 0.26 | 1.92 | 3.42 | 2.6 | 2.6 | 2.4 |  | 1500 |  | 24220 | 0.2 |  | 3.36 | 2.2 |  | 2.1 | 62.26% | 86.44% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 6749789 | HRCU-A-CB | 4A6V0024A1 | *AM8C0B30V21 | 24200 | 13.75 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 6749791 | HRCU-A-CB | 4A6V0048A1 | *AM8C0C48V41 | 47000 | 12.5 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z
Trane | Trane |  | 6749942 | HRCU-A-CB | 4TWV0024A1 | *AM8C0B30V21 | 24200 | 13.75 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A
Trane | Trane |  | 6749944 | HRCU-A-CB | 4TWV0048A1 | *AM8C0C48V41 | 47000 | 12.5 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 6750232 | HRCU-A-CB | 4A6V8036A1 | *AM8C0C36V31 | 35000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 |  | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 |  | 16488 |  | 19680 | 2.66 |  | 3.18 | 1.82 |  | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6750233 | HRCU-A-CB | 4A6V8048A1 | *AM8C0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 |  | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 |  | 22792 |  | 27080 | 3.66 |  | 4.38 | 1.82 |  | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A |  | z
Trane | Trane |  | 6750234 | HRCU-A-CB | 4TWV8036A1 | *AM8C0C36V31 | 35000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 |  | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 |  | 16488 |  | 19680 | 2.66 |  | 3.18 | 1.82 |  | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A
Trane | Trane |  | 6750235 | HRCU-A-CB | 4TWV8048A1 | *AM8C0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 |  | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 |  | 22792 |  | 27080 | 3.66 |  | 4.38 | 1.82 |  | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 6750455 | HRCU-A-CB | 4A6V8024A1 | *AM8C0B30V21 | 23800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6750457 | HRCU-A-CB | 4A6V8049A1 | *AM8C0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z
Trane | Trane |  | 6750459 | HRCU-A-CB | 4TWV8024A1 | *AM8C0B30V21 | 23800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A
Trane | Trane |  | 6750461 | HRCU-A-CB | 4TWV8049A1 | *AM8C0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 6796524 | HRCU-A-CB | 4A6V0036A1 | *UD2C080ACV4 4TXCC007CC3 | 34600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 6796526 | HRCU-A-CB | 4A6V0036A1 | *UD2C100ACV5 4TXCC007CC3 | 34800 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 6796528 | HRCU-A-CB | 4A6V0036A1 | *UD2C080ACV4 4TXFH036CZ3 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6796559 | HRCU-A-CB | 4A6V8037A1 | *AM8C0B30V21 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.66 |  | 3.16 | 1.84 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6796560 | HRCU-A-CB | 4A6V8037A1 | *UD2B080ACV3 4TXCB004CC3 | 34800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 |  | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 |  | 16934 |  | 20240 | 2.8 |  | 3.32 | 1.78 |  | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6796562 | HRCU-A-CB | 4A6V8037A1 | *UD2C080ACV4 4TXCC007CC3 | 34600 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6796563 | HRCU-A-CB | 4A6V8037A1 | *UD2C100ACV5 4TXCC007CC3 | 34800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 6796565 | HRCU-A-CB | 4A6V8037A1 | *UD2C080ACV4 4TXFH036CZ3 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z
Trane | Trane |  | 6796600 | HRCU-A-CB | 4TWV0036A1 | *UD2C080ACV4 4TXCC007CC3 | 34600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A
Trane | Trane |  | 6796602 | HRCU-A-CB | 4TWV0036A1 | *UD2C100ACV5 4TXCC007CC3 | 34800 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A
Trane | Trane |  | 6796604 | HRCU-A-CB | 4TWV0036A1 | *UD2C080ACV4 4TXFH036CZ3 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A
Trane | Trane |  | 6796635 | HRCU-A-CB | 4TWV8037A1 | *AM8C0B30V21 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.66 |  | 3.16 | 1.84 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A
Trane | Trane |  | 6796636 | HRCU-A-CB | 4TWV8037A1 | *UD2B080ACV3 4TXCB004CC3 | 34800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 |  | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 |  | 16934 |  | 20240 | 2.8 |  | 3.32 | 1.78 |  | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A
Trane | Trane |  | 6796638 | HRCU-A-CB | 4TWV8037A1 | *UD2C080ACV4 4TXCC007CC3 | 34600 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A
Trane | Trane |  | 6796639 | HRCU-A-CB | 4TWV8037A1 | *UD2C100ACV5 4TXCC007CC3 | 34800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A
Trane | Trane |  | 6796641 | HRCU-A-CB | 4TWV8037A1 | *UD2C080ACV4 4TXFH036CZ3 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936995 | HRCU-A-CB-O | AOU9RLFF | AGU9RLF | 9000 | 16 | 26 | 12.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.2 | 0.78 | 1.82 | 3.4 | 2.8 | 2.25 |  | 2115 |  | 14000 | 0.19 |  | 2.1 | 3.26 |  | 1.95 | 74.47% | 100% | N/A |  |  | -5 | 2047 | z | 12500 | 0.22 | 2 | 2.73 | 1.83
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936996 | HRCU-A-CB-O | AOU12RLFF | AGU12RLF | 12000 | 13.1 | 22.7 | 11.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.24 | 1.19 | 2.17 | 3 | 2.6 | 2.02 |  | 2423 |  | 15000 | 0.24 |  | 2.17 | 2.96 |  | 2.02 | 76.92% | 100% | N/A |  |  | -5 | 2115 | z | 13000 | 0.22 | 2.06 | 2.82 | 1.85
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936997 | HRCU-A-CB-O | AOU15RLFF | AGU15RLF | 14200 | 12.5 | 20.3 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.32 | 1.3 | 2.89 | 2.59 | 2.62 | 1.93 |  | 2798 |  | 18500 | 0.26 |  | 2.91 | 3.15 |  | 1.86 | 88.94% | 97.37% | N/A |  |  | -5 | 2593 | z | 17500 | 0.26 | 2.86 | 2.92 | 1.79
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937309 | HRCU-A-CB-O | AOU9RLFFH | AGU9RLF | 9000 | 16 | 26 | 12.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.35 | 0.78 | 1.97 | 1.94 | 2.8 | 2.08 |  | 2115 |  | 14000 | 0.34 |  | 2.25 | 1.82 |  | 1.82 | 74.47% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1843 | z | 11000 | 0.38 | 2.07 | 1.42 | 1.56
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937310 | HRCU-A-CB-O | AOU12RLFFH | AGU12RLF | 12000 | 13.1 | 22.7 | 11.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.39 | 1.19 | 2.32 | 1.85 | 2.6 | 1.89 |  | 2423 |  | 15000 | 0.39 |  | 2.32 | 1.82 |  | 1.89 | 76.92% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2252 | z | 14000 | 0.48 | 2.99 | 1.38 | 1.37
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937311 | HRCU-A-CB-O | AOU15RLFFH | AGU15RLF | 14200 | 12.5 | 20.3 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.47 | 1.3 | 3.04 | 1.77 | 2.62 | 1.83 |  | 2798 |  | 18500 | 0.41 |  | 3.06 | 2 |  | 1.77 | 88.94% | 97.37% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2320 | z | 15500 | 0.41 | 2.93 | 1.66 | 1.55
Toshiba Carrier | Carrier |  | 6960758 | N/A | RAS-09EAV-UL | RAS-09EKV-UL | N/A | 13 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 10800 | 16350 | 0.17 | 0.8 | 1.4 | 5.29 | 3.95 | 3.42 |  | 1795 | 6313 | 9551 | 0.127 | 0.61 | 1.042 | 4.14 | 3.03 | 2.69 |  | 1224 |  | 6519 | 0.109 |  | 0.895 | 3.29 |  | 2.13 | 39.87% | 68.25% | N/A |  |  | -4 | 828 |  | 4409 | 0.096 | 0.787 | 2.52 | 1.64
Toshiba Carrier | Carrier |  | 6960762 | N/A | RAS-15EAV-UL | RAS-15EKV-UL | N/A | 13 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 2750 | 18000 | 21500 | 0.143 | 1.4 | 1.9 | 5.64 | 3.77 | 3.32 |  | 1608 | 10400 | 12553 | 0.106 | 1.042 | 1.415 | 4.444 | 2.93 | 2.6 |  | 1096 |  | 8752 | 0.091 |  | 1.215 | 3.52 |  | 2.11 | 40.71% | 69.72% | N/A |  |  | -4 | 742 |  | 5798 | 0.08 | 1.067 | 2.72 | 1.59
Toshiba Carrier | Carrier |  | 6960764 | N/A | RAS-17EAV-UL | RAS-17EKV-UL | N/A | 12.6 | 19 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 2750 | 20200 | 21500 | 0.15 | 1.63 | 1.91 | 5.37 | 3.63 | 3.3 |  | 1608 | 10500 | 12553 | 0.112 | 1.214 | 1.422 | 4.2 | 2.53 | 2.59 |  | 1096 |  | 8572 | 0.096 |  | 1.221 | 3.35 |  | 2.06 | 39.87% | 68.29% | N/A |  |  | -4 | 742 |  | 5798 | 0.084 | 1.073 | 2.59 | 1.58
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961728 | HRCU-A-CB-O | AOU9RLFW1 | ASU9RLF1 | 9000 | 13.8 | 23 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1700 | 12000 | 15000 | 0.25 | 0.89 | 1.6 | 2 | 3.95 | 2.75 |  | 1079 | 7600 | 9500 | 0.2 | 0.71 | 1.27 | 1.59 | 3.1363 | 2.1917 |  | 969 |  | 8530 | 0.19944 |  | 1.27 | 1.4236 |  | 1.9679 | 56.87% | 89.79% | N/A |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961729 | HRCU-A-CB-O | AOU12RLFW1 | ASU12RLF1 | 12000 | 12.5 | 22 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19100 | 0.25 | 1.28 | 1.99 | 3.6 | 3.66 | 2.8122 |  | 1795 | 9400 | 11200 | 0.19 | 0.96 | 1.4925 | 2.8 | 2.869 | 2.196 |  | 1949 |  | 12150 | 0.22266 |  | 1.7723 | 2.57 |  | 2.0071 | 63.61% | 108.5% | N/A |  |  | N/A
Haier | Haier | Novel Series | 6970203 | HRCU-A-CB-O | HSU09VHG(DB)-W | HSU09VHG(DB)-G | 8500 | 13 | 18 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 9000 | 10140 | 0.27 | 0.65 | 0.82 | 4.342 | 4.0581 | 3.6242 |  | 3200 | 5600 | 7190 | 0.27 | 0.52 | 0.64 | 3.4736 | 3.1563 | 3.2926 |  | 2800 |  | 6000 | 0.27 |  | 0.75 | 3.0394 |  | 2.3447 | 59.17% | 83.45% | N/A |  |  | N/A |  | z
Haier | Haier | Novel Series | 6970204 | HRCU-A-CB-O | HSU12VHG(DB)-W | HSU12VHG(DB)-G | 11900 | 13 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4780 | 12600 | 14190 | 0.271 | 0.97 | 1.12 | 5.16 | 3.8071 | 3.71 |  | 3750 | 9000 | 10070 | 0.37 | 1.12 | 1.2 | 2.91 | 2.34 | 2.45 |  | 2380 |  | 6930 | 0.24 |  | 0.88 | 2.82 |  | 2.3 | 48.84% | 68.82% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 6992577 | HRCU-A-CB | 4A6V0036A1 | *AM8C0B30V21 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.64 |  | 3.16 | 1.86 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z
Trane | Trane |  | 6992578 | HRCU-A-CB | 4TWV0036A1 | *AM8C0B30V21 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.64 |  | 3.16 | 1.86 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A
Friedrich Air Conditioning | Friedrich | J-Series | 7000021 | HRCU-A-CB-O | MR09Y3J | MW09Y3J | 9000 | 13.3 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10800 | 17061 | 0.2 | 0.7 | 1.39 | 4.34 | 4.52 | 3.6 |  | 2700 | 5880 | 15355 | 0.27 | 0.56 | 1.9 | 2.89 | 3.08 | 2.37 |  | 2070 |  | 11942.7 | 0.28 |  | 1.95 | 2.16 |  | 1.79 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z
Friedrich Air Conditioning | Friedrich | J-Series | 7000022 | HRCU-A-CB-O | MR12Y3J | MW12Y3J | 11200 | 12.5 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13300 | 22178 | 0.19 | 1 | 2.08 | 4.49 | 3.9 | 3.12 |  | 2700 | 6880 | 19960 | 0.26 | 0.81 | 2.85 | 3.04 | 2.49 | 2.05 |  | 2070 |  | 15524.6 | 0.266 |  | 2.91 | 2.28 |  | 2 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002062 | HRCU-A-CB-O | MUZ-FH09NA | MSZ-FH09NA | 9000 | 16.1 | 30.5 | 13.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 10900 | 18000 | 0.11 | 0.71 | 1.47 | 4.263 | 4.5 | 3.59 |  | 920 | 6700 | 12200 | 0.08 | 0.6 | 1.44 | 3.37 | 3.27 | 2.48 |  | 640 |  | 10900 | 0.06 |  | 1.35 | 3.13 |  | 2.32 | 60.56% | 89.34% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 |  | 7300 | 0.03 | 1.25 | 2.34 | 1.71
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002063 | HRCU-A-CB-O | MUZ-FH12NA | MSZ-FH12NA | 12000 | 13.8 | 26.1 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8000 | 13600 | 0.2 | 0.72 | 1.9 | 3.08 | 3.26 | 2.1 |  | 1450 |  | 13600 | 0.15 |  | 1.8 | 2.83 |  | 2.21 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 550 |  | 9900 | 0.07 | 1.6 | 2.3 | 1.81
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7002444 | HRCU-A-CB-O | MUZ-FH15NA | MSZ-FH15NA | 15000 | 12.5 | 22 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5150 | 18000 | 24000 | 0.43 | 1.3 | 3.36 | 3.5102 | 4.06 | 2.09 |  | 2950 | 11000 | 18000 | 0.31 | 1.02 | 2.48 | 2.79 | 3.16 | 2.13 |  | 2050 |  | 18000 | 0.23 |  | 2.95 | 2.61 |  | 1.79 | 75% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 |  | 14600 | 0.11 | 2.35 | 2 | 1.82
LG Electronics USA, Inc | LG |  | 7012586 | HRCU-A-CB-O | LSU240HLV | LSN240HLV | 22000 | 12.5 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 27000 | 38898 | 0.3 | 2.38 | 4.1 | 3 | 3.3 | 2.8 |  | 2250 | 16570 | 27410 | 0.26 | 1.92 | 3.42 | 2.5 | 2.5 | 2.3 |  | 1500 |  | 23690 | 0.2 |  | 3.36 | 2.2 |  | 2.1 | 60.9% | 86.43% | N/A |  |  | N/A |  | z
Friedrich Air Conditioning | Friedrich | J-Series | 7012589 | HRCU-A-CB-O | MR24Y3J | MW24Y3J | 22000 | 12.5 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6200 | 27000 | 38898 | 0.53 | 2.38 | 4.19 | 3.43 | 3.4 | 2.72 |  | 5456 | 17240 | 34230 | 0.58 | 1.92 | 4.61 | 2.76 | 2.63 | 2.18 |  | 4278 |  | 27228.6 | 0.6 |  | 4.42 | 2.08 |  | 1.8 | 70% | 79.55% | N/A |  |  | N/A |  | z
Carrier | Bryant | Evolution Series | 7029861 | N/A | 280ANV060000 | FE4ANB006L |  | 12.7 | 18 | 12 | Yes | Centrally Ducted | N/A | N/A | 24690 | 55500 | 55500 | 1.75 | 4.2165 | 4.2165 | 4.14 | 3.86 | 3.86 |  | 24160 | 52500 | 52500 | 2.93 | 6.9351 | 6.9351 | 2.42 | 2.22 | 2.22 |  | 19480 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A |  | z
Carrier | Bryant | Evolution Series | 7029862 | N/A | 280ANV036000 | FE4ANB006L |  | 14.5 | 20.5 | 13 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.23 | 2.23 | 4.12 | 4.4 | 4.4 |  | 13250 | 31600 | 31600 | 1.83 | 3.65 | 3.65 | 2.12 | 2.54 | 2.54 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.66 |  | 2.2 | 70.66% | 74.68% | N/A |  |  | N/A |  | z
Carrier | Bryant | Evolution Series | 7029863 | N/A | 280ANV048000 | FE4ANB006L |  | 13.5 | 18.3 | 12.5 | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 3.2386 | 3.2386 | 4.49 | 4.12 | 4.12 |  | 23840 | 47500 | 47500 | 2.66 | 3.35 | 6.27 | 2.6283 | 2.22 | 2.22 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.21 |  | 2.24 | 83.67% | 80.15% | N/A |  |  | N/A |  | z
Carrier | Bryant | Evolution Series | 7029864 | N/A | 280ANV024000 | FE4ANB006L |  | 16 | 20.5 | 13 | Yes | Centrally Ducted | N/A | N/A | 14510 | 23600 | 24800 | 0.85 | 1.47 | 1.47 | 5.01 | 4.7 | 4.7 |  | 13740 | 24800 | 24800 | 1.54 | 2.86 | 2.86 | 2.62 | 2.54 | 2.54 |  | 10930 |  | 19630 | 1.47 |  | 2.77 | 1.73 |  | 2.08 | 79.15% | 79.15% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 7035709 | HRCU-A-CB | 4A6V8036A1 | *DD2C100ACV5 4NXCC005AS3 | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 |  | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 |  | 16828 |  | 20200 | 2.7 |  | 3.26 | 1.82 |  | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A |  | z
Trane | Trane |  | 7035765 | HRCU-A-CB | 4TWV8036A1 | *DD2C100ACV5 4NXCC005AS3 | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 |  | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 |  | 16828 |  | 20200 | 2.7 |  | 3.26 | 1.82 |  | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 7070719 | HRCU-A-CB-O | GWH24QE-D3DNA1D/O | GWH24QE-D3DN***/I | 22000 | 12.5 | 20 | 10 | Yes | Ductless | Singlezone | Mini-Splits | 6203 | 23000 | 25100 | 0.455 | 2.011 | 2.405 | 3.9954 | 3.3922 | 3.0587 |  | 5850 | 14600 | 23450 | 0.555 | 1.643 | 3.607 | 3.0891 | 2.6116 | 1.9053 |  | 7544.4 |  | 22861.5 | 1.1 |  | 3.32 | 2.01 |  | 2.0181 | 91.08% | 97.49% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
Friedrich Air Conditioning | Friedrich | J-Series | 7086358 | HRCU-A-CB-O | MRH12Y3J | MWH12Y3J | 12000 | 14.1 | 25 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 13300 | 13600 | 13950 | 0.956 | 0.983 | 1.09 | 4.0772 | 4.0547 | 3.7508 |  | 8500 | 8800 | 9100 | 0.809 | 0.831 | 0.855 | 3.0792 | 3.1035 | 3.1192 |  | 7000 |  | 7500 | 0.901 |  | 0.95 | 2.2769 |  | 2.3137 | 53.76% | 82.42% | N/A |  |  | -13° | 6300 |  | 6556 | 1.096 | 1.25 | 1.6846 | 1.5371
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 7091967 | HRCU-A-CB-O | GWH09QC-A3DNA1D/O | GWH09QC-A3DN***/I | 9000 | 13 | 23 | 10.5 | Yes | Ductless | Singlezone | Mini-Splits | 2100 | 9900 | 14000 | 0.1 | 0.7 | 1.27 | 6.1545 | 4.1449 | 3.2307 |  | 1825 | 6100 | 10215 | 0.1 | 0.75 | 1.271 | 5.3485 | 3.2906 | 2.3554 |  | 1545 |  | 8680 | 0.1 |  | 1.252 | 4.5279 |  | 2.0318 | 62% | 84.97% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 7091968 | HRCU-A-CB-O | GWH12QC-A3DNA1D/O | GWH12QC-A3DN***/I | 12000 | 12.5 | 22 | 10.2 | Yes | Ductless | Singlezone | Mini-Splits | 2854 | 12200 | 16582 | 0.17 | 1.05 | 1.45 | 4.9201 | 3.4465 | 3.3515 |  | 2478 | 6800 | 10348 | 0.15 | 0.804 | 1.37 | 4.8415 | 2.486 | 2.2136 |  | 2085 |  | 8611 | 0.13 |  | 1.323 | 4.7004 |  | 1.9075 | 51.93% | 83.21% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 7091970 | HRCU-A-CB-O | GWH09QC-D3DNA1D/O | GWH09QC-D3DN***/I | 9000 | 14 | 23 | 10.5 | Yes | Ductless | Singlezone | Mini-Splits | 1900 | 11000 | 12000 | 0.16 | 1.02 | 1.35 | 3.4802 | 3.1606 | 2.6051 |  | 1750 | 6800 | 11546 | 0.13 | 0.98 | 1.548 | 3.9452 | 2.0336 | 2.1859 |  | 1450 |  | 9171 | 0.1 |  | 1.334 | 4.2495 |  | 2.0148 | 76.42% | 79.43% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 7091971 | HRCU-A-CB-O | GWH12QC-D3DNA1D/O | GWH12QC-D3DN***/I | 12000 | 12.5 | 22 | 11 | Yes | Ductless | Singlezone | Mini-Splits | 2921 | 13000 | 14000 | 0.21 | 1.084 | 1.4 | 4.0765 | 3.5496 | 2.9307 |  | 2610 | 7100 | 10954 | 0.19 | 0.844 | 1.341 | 4.0259 | 2.5803 | 2.394 |  | 2376 |  | 8800 | 0.18 |  | 1.276 | 3.8685 |  | 2.0212 | 62.86% | 80.34% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
American Standard | American Standard | AccuComfort Platinum 20 | 7125570 | HRCU-A-CB | 4A6V0036A1 | *UHMB060ACV3 4TXCB004CC3 | 34800 | 12.5 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 |  | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 |  | 16934 |  | 20300 | 2.82 |  | 3.36 | 1.76 |  | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 7125571 | HRCU-A-CB | 4A6V0036A1 | *UHMB060ACV3 4TXFH036CZ3 | 34800 | 12.5 | 18.75 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 |  | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 |  | 16788 |  | 20040 | 2.78 |  | 3.32 | 1.76 |  | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 7125572 | HRCU-A-CB | 4A6V0036A1 | *DHMB060BCV3 4TXFH036CZ3 | 34800 | 12.5 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 |  | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 7125581 | HRCU-A-CB | 4A6V8037A1 | *DHMB060BCV3 4TXFH036CZ3 | 34800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 |  | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z
Trane | Trane |  | 7125586 | HRCU-A-CB | 4TWV0036A1 | *UHMB060ACV3 4TXCB004CC3 | 34800 | 12.5 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 |  | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 |  | 16934 |  | 20300 | 2.82 |  | 3.36 | 1.76 |  | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A
Trane | Trane |  | 7125587 | HRCU-A-CB | 4TWV0036A1 | *UHMB060ACV3 4TXFH036CZ3 | 34800 | 12.5 | 18.75 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 |  | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 |  | 16788 |  | 20040 | 2.78 |  | 3.32 | 1.76 |  | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A
Trane | Trane |  | 7125588 | HRCU-A-CB | 4TWV0036A1 | *DHMB060BCV3 4TXFH036CZ3 | 34800 | 12.5 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 |  | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A
Trane | Trane |  | 7125597 | HRCU-A-CB | 4TWV8037A1 | *DHMB060BCV3 4TXFH036CZ3 | 34800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 |  | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A
American Standard | American Standard |  | 7151530 | HRCU-A-CB-O | 4TXK2709A10N0AA | 4MXW2709A10N0AA | 9000 | 14.5 | 27 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 |  | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 |  | 1480 |  | 8000 | 0.15 |  | 1.095 | 2.8916 |  | 2.1412 | 72.73% | 75.25% | Integrated | 72W | Heater on below 34°F | N/A |  | z
Trane | Trane |  | 7151531 | HRCU-A-CB-O | 4TXK2709A10N0AA | 4MXW2709A10N0AA | 9000 | 14.5 | 27 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 |  | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 |  | 1480 |  | 8000 | 0.15 |  | 1.095 | 2.8916 |  | 2.1412 | 72.73% | 75.25% | Integrated | 72 | Heater on below 34°F | N/A
American Standard | American Standard |  | 7151532 | HRCU-A-CB-O | 4TXK2712A10NAA | 4MXW2712A10N0AA | 12000 | 13 | 25 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 |  | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 |  | 2100 |  | 8300 | 0.085 |  | 1.131 | 7.2406 |  | 2.1507 | 59.29% | 95.4% | Integrated | 72W | Heater on below 34°F | N/A |  | z
Trane | Trane |  | 7151533 | HRCU-A-CB-O | 4TXK2712A10NAA | 4MXW2712A10N0AA | 12000 | 13 | 25 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 |  | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 |  | 2100 |  | 8300 | 0.085 |  | 1.131 | 7.2406 |  | 2.1507 | 59.29% | 95.4% | Integrated | 72 | Heater on below 34°F | N/A
American Standard | American Standard |  | 7151534 | HRCU-A-CB-O | 4TXK2718A10N0AA | 4MXW2718A10N0AA | 18000 | 12.5 | 21 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 |  | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 |  | 2388 |  | 15400 | 0.42 |  | 2.29 | 1.6663 |  | 1.9709 | 66.37% | 78.28% | Integrated | 160W | Heater on below 34°F | N/A
Trane | Trane |  | 7151535 | HRCU-A-CB-O | 4TXK2718A10N0AA | 4MXW2718A10N0AA | 18000 | 12.5 | 21 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 |  | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 |  | 2388 |  | 15400 | 0.42 |  | 2.29 | 1.6663 |  | 1.9709 | 66.37% | 78.28% | Integrated | 160 | Heater on below 34°F | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 7161151 | HRCU-A-CB | 4A6V0048A1 | *AM8C0C60V51 | 46500 | 12.5 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 |  | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 |  | 22486 |  | 26780 | 3.64 |  | 4.34 | 1.8 |  | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A |  | z
Trane | Trane |  | 7161152 | HRCU-A-CB | 4TWV0048A1 | *AM8C0C60V51 | 46500 | 12.5 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 |  | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 |  | 22486 |  | 26780 | 3.64 |  | 4.34 | 1.8 |  | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A
LG Electronics USA, Inc | LG |  | 7180062 | HMSV-A-CB | LMU24CHV | Non-Ducted Indoor Units | 20000 | 13.5 | 21.7 | 10.6 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 24000 | 28800 | 1.092 | 1.8 | 2.52 | 2.5 | 3.9 | 3.3 |  | 5580 | 14500 | 21097 | 0.945 | 1.56 | 1.71 | 1.7 | 2.7 | 3.6 |  | 4332 |  | 14595 | 0.917 |  | 1.65 | 1.4 |  | 2.6 | 50.68% | 69.18% | Optional Accessory #PQSH1200 | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 7180063 | HMSV-A-CB | LMU36CHV | Non-Ducted Indoor Units | 32000 | 13 | 22 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 36000 | 41600 | 1.127 | 2.74 | 3.836 | 2.4 | 3.9 | 3.2 |  | 5658 | 20000 | 29105 | 0.924 | 2.24 | 2.79 | 1.8 | 2.6 | 3.1 |  | 4446 |  | 22057 | 0.868 |  | 2.6 | 1.5 |  | 2.5 | 53.02% | 75.78% | Optional Accessory #PQSH1200 | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 7184507 | HMSV-A-CB | LMU24CHV | Mixed | 18900 | 12.5 | 19.6 | 10.2 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 10230 | 23250 | 27900 | 1.171 | 1.859 | 2.6 | 2.6 | 3.7 | 3.1 |  | 6270 | 14250 | 20394 | 1.008 | 1.61 | 1.76 | 1.8 | 2.6 | 3.4 |  | 4932 |  | 14109 | 0.973 |  | 1.7 | 1.5 |  | 2.4 | 50.57% | 69.18% | Optional Accessory #PQSH1200 | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434477 | HMSV-A-CB | MXZ-5C42NAHZ | Non-Ducted Indoor Units | 42000 | 13.4 | 19 | 11 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 24000 | 48000 | 48000 | 1.17 | 3.43 | 3.43 | 6.01 | 4.1 | 4.1 |  | 24000 | 35800 | 48000 | 1.66 | 3.65 | 4.87 | 4.23 | 2.87 | 2.89 |  | 24000 |  | 48000 | 1.91 |  | 5.61 | 3.69 |  | 2.51 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 24000 |  | 36000 | 2.5 | 4.8 | 2.81 | 2.2
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434482 | HMSV-A-CB | MXZ-4C36NAHZ | Non-Ducted Indoor Units | 36000 | 14 | 19.1 | 11.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 22500 | 45000 | 45000 | 1.09 | 3.34 | 3.34 | 6.05 | 3.95 | 3.95 |  | 22500 | 34000 | 45000 | 1.55 | 3.5 | 4.74 | 4.26 | 2.85 | 2.78 |  | 22500 |  | 45000 | 1.78 |  | 5.46 | 3.71 |  | 2.41 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 22500 |  | 33800 | 2.33 | 4.68 | 2.83 | 2.12
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434486 | HMSV-A-CB | MXZ-4C36NAHZ | Mixed | 36000 | 12.65 | 17.45 | 10.7 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 22500 | 45000 | 45000 | 1.3 | 3.8 | 3.8 | 5.07 | 3.48 | 3.48 |  | 22500 | 35000 | 45000 | 2.15 | 4.05 | 5.35 | 3.07 | 2.54 | 2.47 |  | 22500 |  | 45000 | 2.62 |  | 6.21 | 2.52 |  | 2.16 | 100% | 100% | N/A |  |  | -13 | 22500 |  | 33800 | 3.14 | 5.32 | 2.1 | 1.89
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7451794 | N/A | MXZ-3C30NAHZ | Non-Ducted Indoor Units |  | 12.5 | 18 | 11 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 |  | 25225 | 1.4 | 4.49 | 2.09 | 1.64
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7451969 | N/A | MXZ-3C24NAHZ | Non-Ducted Indoor Units |  | 13.5 | 19 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 |  | 22050 | 1.4 | 3.52 | 2.09 | 1.83
LG Electronics USA, Inc | LG |  | 7484109 | HRCU-A-CB-O | LSU090HSV4 | LAN090HSV4 | 9000 | 13.3 | 21.5 | 10.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 10800 | 17061 | 0.075 | 0.7 | 1.43 | 4 | 4.5 | 3.5 |  | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.6635 | 3.2 |  | 500 |  | 9570 | 0.05 |  | 1 | 2.9 |  | 2.8 | 56.09% | 86.37% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 7484110 | HRCU-A-CB-O | LSU090HSV4 | LSN090HSV4 | 9000 | 13.3 | 21.5 | 10.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 10800 | 17061 | 0.07 | 0.7 | 1.35 | 4.3 | 4.5 | 3.7 |  | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.6635 | 3.2 |  | 500 |  | 9570 | 0.05 |  | 1 | 2.9 |  | 2.8 | 56.09% | 86.37% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 7484111 | HRCU-A-CB-O | LSU120HSV4 | LAN120HSV4 | 11200 | 12.5 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 |  | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3.1402 | 2.7 |  | 500 |  | 11670 | 0.054 |  | 1.41 | 2.7 |  | 2.4 | 52.62% | 86.44% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 7484112 | HRCU-A-CB-O | LSU120HSV4 | LSN120HSV4 | 11200 | 12.5 | 21.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 |  | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3.1402 | 2.7 |  | 500 |  | 11670 | 0.054 |  | 1.41 | 2.7 |  | 2.4 | 52.62% | 86.44% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 7599436 | HRCU-A-CB | 4A6V0036A1 | *AM8C0C48V41 | 36000 | 13.5 | 20.75 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 |  | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 |  | 16548 |  | 19800 | 2.54 |  | 3 | 1.9 |  | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A |  | z
Trane | Trane |  | 7599437 | HRCU-A-CB | 4TWV0036A1 | *AM8C0C48V41 | 36000 | 13.5 | 20.75 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 |  | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 |  | 16548 |  | 19800 | 2.54 |  | 3 | 1.9 |  | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607465 | HRCU-A-CB-O | GWH09UC-D3DNA4C/O | GWH09UC-D3DN***/I | 9000 | 15.7 | 30.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.35 | 3.4993 | 4.324 | 2.8743 |  | 2388 | 5500 | 13240 | 0.2 | 0.56 | 1.35 | 3.4993 | 2.8784 | 2.8743 |  | 2388 |  | 10488 | 0.4 |  | 1.55 | 1.7496 |  | 1.9831 | 79.21% | 79.21% | Integrated | 72 | Heater on below 34°F of outdoor temperature | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607467 | HRCU-A-CB-O | GWH12UC-D3DNA4C/O | GWH12UC-D3DN***/I | 12000 | 12.7 | 23 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.21 | 1.22 | 4.5001 | 3.1487 | 3.1229 |  | 3071 | 13000 | 13000 | 0.2 | 1.21 | 1.22 | 4.5001 | 3.1487 | 3.1229 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.2501 |  | 2.7608 | 100% | 100% | Integrated | 72 | Heater on below 34°F of outdoor temperature | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607469 | HRCU-A-CB-O | GWH18UC-D3DNA4C/O | GWH18UC-D3DN***/I | 18000 | 12.5 | 21 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.8 | 2.5 | 3.1426 | 3.0935 | 2.8798 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.1426 | 2.5013 | 2.8798 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.9998 |  | 2.8548 | 78.12% | 78.12% | Integrated | 72 | Heater on below 34°F of outdoor temperature | N/A
LG Electronics USA, Inc | LG |  | 7849625 | HRCU-A-CB-O | LAU120HYV1 | LAN120HYV1 | 11000 | 13.8 | 25.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 12000 | 22178 | 0.06 | 0.75 | 1.39 | 5 | 4.7 | 4.7 |  | 676 | 7360 | 14650 | 0.07 | 0.61 | 1.5 | 2.8 | 2.8303 | 2.9 |  | 633 |  | 13720 | 0.07 |  | 1.47 | 2.7 |  | 2.7 | 61.86% | 93.65% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLB Series | 7937663 | HRCU-A-CB-O | AOU18RLB | ASU18RLB | 18000 | 12.5 | 19 | 10.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20000 | 0.17 | 1.285 | 2.06 | 5.29 | 4.11 | 2.8447 |  | 2798 | 11500 | 16700 | 0.2 | 1.15 | 2.1 | 4.0991 | 2.92 | 2.3327 |  | 2696 |  | 15400 | 0.21 |  | 2.18 | 3.76 |  | 2.0698 | 77% | 92.22% | N/A |  |  | N/A
LG Electronics USA, Inc | LG |  | 7947563 | HRCU-A-CB-O | LAU090HYV1 | LAN090HYV1 | 9000 | 15.65 | 27.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 11000 | 20472 | 0.07 | 0.71 | 1.32 | 4.3 | 4.5 | 4.5 |  | 597 | 6750 | 11940 | 0.06 | 0.57 | 1.16 | 2.9 | 2.9162 | 3 |  | 561 |  | 11220 | 0.06 |  | 1.14 | 2.7 |  | 2.9 | 54.81% | 93.97% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Panasonic | Panasonic | Exterios-Series | 7958198 | HRCU-A-CB-O | CS-E9RKUA | CU-E9RKUAW | 9000 | 13 | 23 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 12000 | 14100 | 0.2 | 1.12 | 1.5 | 6 | 3.14 | 2.76 |  | 3200 | 8100 | 9500 | 0.19 | 0.99 | 1.33 | 4.939 | 2.3994 | 2.1 |  | 2400 |  | 8300 | 0.16 |  | 1.32 | 4.3988 |  | 1.844 | 58.87% | 87.37% | N/A |  |  | -5°F | 1600 |  | 7000 | 0.13 | 1.31 | 3.6093 | 1.567
Panasonic | Panasonic | Exterios-Series | 7958199 | HRCU-A-CB-O | CS-E12RKUA | CU-E12RKUAW | 11500 | 12.5 | 22.5 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 13800 | 16300 | 0.2 | 1.25 | 1.71 | 6 | 3.24 | 2.79 |  | 3200 | 8900 | 10500 | 0.19 | 1.05 | 1.44 | 4.939 | 2.4857 | 2.14 |  | 2400 |  | 9100 | 0.16 |  | 1.51 | 4.3988 |  | 1.7673 | 55.83% | 86.67% | N/A |  |  | -5°F | 1600 |  | 7900 | 0.13 | 1.6 | 3.6093 | 1.4479
Panasonic | Panasonic | Exterios E:Deluxe | 7958200 | HRCU-A-CB-O | CS-E18RKUA | CU-E18RKUAW | 17200 | 13.2 | 19.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 21600 | 22000 | 0.38 | 1.75 | 1.8 | 4.47 | 3.62 | 3.57 |  | 3400 | 11600 | 12000 | 0.34 | 1.3 | 1.35 | 2.9326 | 2.6167 | 2.6 |  | 2600 |  | 10100 | 0.3 |  | 1.32 | 2.5415 |  | 2.2438 | 45.91% | 84.17% | N/A |  |  | -5°F | 1900 |  | 8200 | 0.26 | 1.29 | 2.143 | 1.8641
Carrier | Carrier |  | 7992954 | HRCU-A-CB-O | 38GRQB09---301 | 40GRQB09H--301 | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.4994 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
Carrier | Carrier |  | 7992956 | HRCU-A-CB-O | 38GRQB12---301 | 40GRQB12H--301 | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5003 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
Carrier | Carrier |  | 7992958 | HRCU-A-CB-O | 38GRQB18---301 | 40GRQB18H--301 | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.1427 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993242 | HRCU-A-CB-O | AOU12RLS3 | ASU12RLS3 | 12000 | 15.2 | 29.3 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5428 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 | 74.63% | 94.29% | N/A |  |  | -5 | 2081 | z | 15000 | 0.22 | 2.09 | 2.77 | 2.1
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993243 | HRCU-A-CB-O | AOU15RLS3 | ASU15RLS3 | 14500 | 13.9 | 25.3 | 13.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 | 85.77% | 95.35% | N/A |  |  | -5 | 2388 | z | 18500 | 0.21 | 2.74 | 3.33 | 1.98
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993244 | HRCU-A-CB-O | AOU12RLS3H | ASU12RLS3 | 12000 | 15.2 | 29.3 | 13.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 | 74.63% | 94.29% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1638 | z | 11500 | 0.38 | 2.23 | 1.26 | 1.51
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 7993245 | HRCU-A-CB-O | AOU15RLS3H | ASU15RLS3 | 14500 | 13.9 | 25.3 | 13.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 | 85.77% | 95.35% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2081 | z | 16000 | 0.37 | 2.88 | 1.65 | 1.63
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Lomo 23 Series | 8000864 | HRCU-A-CB-O | GWH18QD-D3DNA1G/O | GWH18QD-D3DN***/I | 18000 | 12.5 | 20 | 10.5 | Yes | Ductless | Singlezone | Mini-Splits | 8697 | 19800 | 23533 | 0.653 | 1.681 | 2.425 | 3.9033 | 3.4537 | 2.8441 |  | 4050 | 12400 | 18688 | 0.351 | 1.37 | 2.613 | 3.3816 | 2.6678 | 2.096 |  | 5435 |  | 16425 | 0.75 |  | 2.622 | 2.1238 |  | 1.8359 | 69.8% | 87.89% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 2018-02-05
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 8004699 | HRCU-A-CB-O | AOU9RLS3 | ASU9RLS3 | 9000 | 18 | 33 | 14.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 | 68.18% | 93.75% | N/A |  |  | -5 | 1945 | z | 13500 | 0.22 | 2.09 | 2.59 | 1.89
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8004700 | HRCU-A-CB-O | AOU9RLS3H | ASU9RLS3 | 9000 | 18 | 33 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 | 68.18% | 93.75% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1535 | z | 11000 | 0.38 | 2.23 | 1.18 | 1.44
Haier | Haier | Advanced Series | 8021588 | HRCU-A-CB-O | 1U12ES2VHA | AW12ES2VHA | 12000 | 12.5 | 23 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 16000 | 19800 | 0.225 | 1.25 | 1.66 | 5.33 | 3.7515 | 3.49 |  | 3550 | 12220 | 13120 | 0.33 | 1.19 | 1.25 | 3.11 | 3 | 3.07 |  | 2960 |  | 10160 | 0.3 |  | 1.21 | 2.85 |  | 2.46 | 51.31% | 77.44% | N/A |  |  | N/A |  | z
Haier | Haier | Advanced Series | 8028490 | HRCU-A-CB-O | 1U18ES2VHA | AW18ES2VHA | 17000 | 12.6 | 21 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5400 | 22000 | 26400 | 0.4 | 1.83 | 2.9 | 3.96 | 3.5234 | 2.67 |  | 4500 | 14000 | 19600 | 0.45 | 1.5 | 2.7 | 2.93 | 2.74 | 2.13 |  | 3800 |  | 14900 | 0.43 |  | 2.1 | 2.59 |  | 2.08 | 56.44% | 76.02% | N/A |  |  | N/A |  | z
Haier | Haier | Advanced Series | 8028525 | HRCU-A-CB-O | 1U24ES2VHA | AW24ES2VHA | 22000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 27700 | 34800 | 0.55 | 2.35 | 3.3 | 3.62 | 3.4546 | 3.09 |  | 5800 | 18500 | 26000 | 0.58 | 1.9 | 3.25 | 2.93 | 2.85 | 2.35 |  | 4700 |  | 20500 | 0.55 |  | 2.8 | 2.51 |  | 2.15 | 58.91% | 78.85% | N/A |  |  | N/A |  | z
Haier | Haier | Advanced Series | 8028528 | HRCU-A-CB-O | 1U09ES2VHA | AW09ES2VHA | 9000 | 14.5 | 23.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 10000 | 15000 | 0.25 | 0.65 | 1.2 | 4.69 | 4.509 | 3.66 |  | 3200 | 7400 | 10800 | 0.27 | 0.63 | 1.1 | 3.54 | 3.44 | 2.88 |  | 2800 |  | 10000 | 0.26 |  | 1.18 | 3.16 |  | 2.48 | 66.67% | 92.59% | N/A |  |  | N/A |  | z
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033584 | HMSV-A-CB | AOU18RLXFZH | Non-Ducted Indoor Units | 18000 | 13.5 | 21.5 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6200 | 22000 | 24400 | 0.52 | 1.7 | 2.02 | 3.85 | 3.8 | 3.54 |  | 6619 | 14200 | 23500 | 0.81 | 1.6 | 3.18 | 2.4 | 2.6 | 2.16 |  | 6210 |  | 22000 | 0.89 |  | 3.49 | 2.04 |  | 1.85 | 90.16% | 93.62% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3378 | z | 12000 | 0.55 | 2.14 | 1.8 | 1.64
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033586 | HMSV-A-CB | AOU24RLXFZH | Non-Ducted Indoor Units | 22000 | 13.3 | 20 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6200 | 25000 | 29800 | 0.5 | 1.81 | 2.85 | 4 | 4.04 | 3.06 |  | 6005 | 15400 | 26000 | 0.62 | 1.73 | 3.57 | 2.84 | 2.6 | 2.13 |  | 5869 |  | 25500 | 0.62 |  | 3.57 | 2.77 |  | 2.09 | 85.57% | 98.08% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3207 | z | 13500 | 0.43 | 2.44 | 2.19 | 1.62
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103542 | HMSV-A-CB | 2MXS18NMVJU | CTXS09HVJU+CTXS09LVJU | 18000 | 12.5 | 18.9 | 10.7 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 4900 | 18900 | 25000 | 0.29 | 1.26 | 1.69 | 4.94 | 4.4 | 4.34 |  | 3800 | 12780 | 16910 | 0.29 | 1.11 | 1.49 | 3.8404 | 3.37 | 3.33 |  | 3190 |  | 13150 | 0.29 |  | 1.4 | 3.21 |  | 2.76 | 52.6% | 77.76% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 2910 | z | 11580 | 0.29 | 1.36 | 2.93 | 2.5
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103869 | HMSV-A-CB | 3MXS24NMVJU | CTXS07LVJU+CTXS09LVJU+CTXS09LVJU | 24000 | 12.7 | 17.9 | 12.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8500 | 24000 | 36000 | 0.43 | 1.46 | 2.97 | 5.79 | 4.82 | 3.55 |  | 6570 | 16230 | 24350 | 0.43 | 1.29 | 2.62 | 4.478 | 3.69 | 2.72 |  | 5500 |  | 18930 | 0.43 |  | 2.46 | 3.75 |  | 2.26 | 52.58% | 77.74% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 5020 | z | 16670 | 0.43 | 2.39 | 3.42 | 2.05
LG Electronics USA, Inc | LG |  | 8111355 | HMSV-A-CB | LMU30CHV | Non-Ducted Indoor Units | 30000 | 13 | 22 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 32000 | 38400 | 1.043 | 2.49 | 3.486 | 2.6 | 3.8 | 3.2 |  | 5658 | 19600 | 26739 | 0.882 | 2.1 | 2.55 | 1.9 | 2.7 | 3.1 |  | 4446 |  | 20622 | 0.84 |  | 2.42 | 1.6 |  | 2.5 | 53.7% | 77.12% | Optional Accessory #PQSH1200 | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
LG Electronics USA, Inc | LG |  | 8111358 | HMSV-A-CB | LMU480HV | Non-Ducted Indoor Units | 48000 | 12.5 | 19.5 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 15840 | 54000 | 61000 | 1.419 | 4.32 | 6.02 | 3.3 | 3.7 | 3 |  | 9996 | 34080 | 49014 | 0.993 | 3.02 | 5.07 | 3 | 3.3 | 2.8 |  | 8076 |  | 38900 | 0.851 |  | 4.52 | 2.8 |  | 2.5 | 63.77% | 79.37% | Optional Accessory #PQSH1200 | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129529 | HRCU-A-CB-O | MPA009S4S-1P | MWMA009S4-1P | 9000 | 14.5 | 23.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3102 | 10000 | 11800 | 0.153 | 0.801 | 1.308 | 5.9419 | 3.6588 | 2.6439 |  | 2388 | 5700 | 8678 | 0.178 | 0.702 | 1.098 | 3.9318 | 2.3796 | 2.3163 |  | 2173 |  | 6291 | 0.167 |  | 0.884 | 3.8134 |  | 2.0856 | 53.31% | 72.49% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129532 | HRCU-A-CB-O | MPA012S4S-1P | MWMA012S4-1P | 12000 | 13 | 21.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3820 | 12000 | 16500 | 0.182 | 1.047 | 1.71 | 6.1513 | 3.359 | 2.8279 |  | 3224 | 7600 | 11920 | 0.226 | 0.844 | 1.484 | 4.1808 | 2.639 | 2.354 |  | 2674 |  | 6292 | 0.196 |  | 0.98 | 3.9983 |  | 1.8816 | 38.13% | 52.79% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129542 | HRCU-A-CB-O | MPA024S4S-1P | MWMA024S4-1P | 23000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7060 | 25000 | 31850 | 0.446 | 2.275 | 3.42 | 4.6392 | 3.2206 | 2.7293 |  | 5597 | 17800 | 18825 | 0.532 | 1.877 | 2.461 | 3.0833 | 2.7793 | 2.2418 |  | 4942 |  | 16382 | 0.483 |  | 2.202 | 2.9987 |  | 2.1803 | 51.43% | 87.02% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129566 | HRCU-A-CB-O | MPA012S4S-1P | M22A012S4-1P | 12000 | 13 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4062 | 12000 | 16916 | 0.195 | 0.93 | 1.702 | 6.1049 | 3.7816 | 2.9128 |  | 7200 | 3178 | 11696 | 0.799 | 0.229 | 1.498 | 2.6409 | 4.0672 | 2.2882 |  | 2716 |  | 7465 | 0.218 |  | 1.143 | 3.6513 |  | 1.9141 | 44.13% | 63.83% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
International Comfort Products | HEIL | High Wall System | 8177081 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.3242 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | KEEPRITE | High Wall System | 8177082 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | TEMPSTAR | High Wall System | 8177083 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | DAY & NIGHT | High Wall System | 8177084 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | ARCOAIRE | High Wall System | 8177085 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | KENMORE | High Wall System | 8177086 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | COMFORTMAKER | High Wall System | 8177087 | HRCU-A-CB-O | DLCAHB09K1A | DLFAHH09K1A | 9000 | 15.7 | 30.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835
International Comfort Products | HEIL | High Wall System | 8177090 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | KEEPRITE | High Wall System | 8177091 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | TEMPSTAR | High Wall System | 8177092 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | DAY & NIGHT | High Wall System | 8177093 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | ARCOAIRE | High Wall System | 8177094 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | KENMORE | High Wall System | 8177095 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | COMFORTMAKER | High Wall System | 8177096 | HRCU-A-CB-O | DLCAHB12K1A | DLFAHH12K1A | 12000 | 12.7 | 23 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99
International Comfort Products | HEIL | High Wall System | 8177099 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | KEEPRITE | High Wall System | 8177100 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | TEMPSTAR | High Wall System | 8177101 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | DAY & NIGHT | High Wall System | 8177102 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | ARCOAIRE | High Wall System | 8177103 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | KENMORE | High Wall System | 8177104 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
International Comfort Products | COMFORTMAKER | High Wall System | 8177105 | HRCU-A-CB-O | DLCAHB18K1A | DLFAHH18K1A | 18000 | 12.5 | 21 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 300 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat 4 Way | 8203107 | HRCU-A-CB-O | AC030JXSCCH/AA | AC030JN4DCH/AA | 30000 | 13.1 | 21 | 10.1 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 13000 | 32000 | 37000 | 0.9 | 2.468 | 3.16 | 4.2332 | 3.7999 | 3.4315 |  | 12500 | 20800 | 36000 | 1.01 | 2.21 | 5.28 | 3.6271 | 2.7583 | 1.9982 |  | 12000 |  | 32000 | 1.32 |  | 5.02 | 2.6643 |  | 1.8682 | 86.49% | 88.89% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13°F | 12000 |  | 28000 | 1.58 | 5.62 | 2.2259 | 1.4601
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat 4 Way | 8203116 | HRCU-A-CB-O | AC036JXSCCH/AA | AC036JN4DCH/AA | 36000 | 12.9 | 20 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 14000 | 40000 | 46000 | 1.02 | 3.238 | 4.2 | 4.0225 | 3.6204 | 3.2098 |  | 13500 | 25000 | 44000 | 1.34 | 2.64 | 6.72 | 2.9526 | 2.7753 | 1.9189 |  | 14000 |  | 40000 | 1.72 |  | 6.6 | 2.3855 |  | 1.7762 | 86.96% | 90.91% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13 | 14000 |  | 32000 | 2 | 6.88 | 2.0515 | 1.3631
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat HSP | 8203117 | HRCU-A-CB | AC030JXSCCH/AA | AC030JNHDCH/AA | 30000 | 13 | 21 | 10.1 | Yes | Centrally Ducted | N/A | N/A | 13000 | 32000 | 37000 | 0.92 | 2.468 | 3.18 | 4.1412 | 3.7999 | 3.4099 |  | 12500 | 20800 | 36000 | 1.11 | 2.33 | 5.38 | 3.3003 | 2.6163 | 1.9611 |  | 12000 |  | 32000 | 1.44 |  | 5.22 | 2.4423 |  | 1.7966 | 86.49% | 88.89% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13°F | 12000 |  | 28000 | 1.71 | 5.88 | 2.0566 | 1.3956
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat HSP | 8203122 | HRCU-A-CB | AC036JXSCCH/AA | AC036JNHDCH/AA | 36000 | 12.8 | 20 | 10.4 | Yes | Centrally Ducted | N/A | N/A | 14000 | 40000 | 46000 | 1.12 | 3.51 | 4.52 | 3.6634 | 3.3398 | 2.9826 |  | 13500 | 25600 | 44000 | 1.48 | 2.94 | 7.02 | 2.6733 | 2.5519 | 1.8369 |  | 14000 |  | 40000 | 1.88 |  | 6.66 | 2.1824 |  | 1.7602 | 86.96% | 90.91% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13 | 14000 |  | 32000 | 2.2 | 7.02 | 1.865 | 1.3359
Lennox Industries | Lennox | Elite XP20 Series | 8550469 | HRCU-A-CB | XP20-036-230A** | CBX32MV-036-230 | 34400 | 13.5 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 10400 | 33200 | 33200 | 0.64 | 3 | 3 | 4.7624 | 3.2433 | 3.2433 |  | 21800 | 21800 | 21800 | 2.7 | 2.7 | 2.7 | 2.3663 | 2.3663 | 2.3663 |  | 19000 |  | 19000 | 2.7 |  | 2.7 | 2.0624 |  | 2.0624 | 57.23% | 87.16% | N/A |  |  | N/A | 0 |  | 0
Lennox Industries | Lennox | Elite XP20 Series | 8550470 | HRCU-A-CB | XP20-036-230A** | CBX40UHV-036-230 | 34400 | 13.5 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 10400 | 33000 | 33000 | 0.64 | 3 | 3 | 4.7624 | 3.2238 | 3.2238 |  | 21800 | 21800 | 21800 | 2.7 | 2.7 | 2.7 | 2.3663 | 2.3663 | 2.3663 |  | 19000 |  | 19000 | 2.6 |  | 2.6 | 2.1417 |  | 2.1417 | 57.58% | 87.16% | N/A |  |  | N/A | 0 |  | 0
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 8584525 | HRCU-A-CB-O | LAU180HYV1 | LAN180HYV1 | 18200 | 13.5 | 24 | 12.5 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 3070 | 22000 | 30709 | 0.55 | 1.69 | 2.49 | 1.6359 | 3.8151 | 3.6144 |  | 2333 | 13000 | 22340 | 0.24 | 1.37 | 2.44 | 2.8489 | 2.781 | 2.6833 |  | 1929 |  | 19300 | 0.24 |  | 2.39 | 2.3556 |  | 2.3666 | 62.85% | 86.39% | Integrated | 120 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 8584526 | HRCU-A-CB-O | LAU240HYV1 | LAN240HYV1 | 22000 | 12.5 | 22 | 12 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 3070 | 27000 | 35200 | 0.55 | 2.2 | 3.24 | 1.6359 | 3.5968 | 3.184 |  | 2333 | 17200 | 27410 | 0.24 | 1.8 | 3.16 | 2.8489 | 2.8005 | 2.5421 |  | 1929 |  | 23690 | 0.24 |  | 3.1 | 2.3556 |  | 2.2396 | 67.3% | 86.43% | Integrated | 120 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series | 8635969 | HRCU-A-CB-O | PUZ-HA36NHA5 | PVA-A36AA* | 33000 | 12.5 | 17.8 | 11 | Yes | Centrally Ducted | N/A | N/A | 18000 | 38000 | 40000 | 1.14 | 3.04 | 3.36 | 4.63 | 3.66 | 3.49 |  | 19000 | 25000 | 38000 | 2.03 | 3.33 | 5.4 | 2.74 | 2.2 | 2.06 |  | 15000 |  | 38000 | 1.73 |  | 6.1 | 2.54 |  | 1.82 | 95% | 100% | N/A |  |  | -13 | 13000 |  | 29000 | 1.77 | 6.15 | 2.15 | 1.38
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635970 | HRCU-A-CB-O | PUZ-HA36NHA5 | PEAD-A36AA* | 33000 | 12.5 | 16.8 | 10.4 | Yes | Centrally Ducted | N/A | N/A | 18000 | 38000 | 40000 | 1.16 | 3.15 | 3.27 | 4.54 | 3.53 | 3.58 |  | 14000 | 27000 | 38000 | 1.54 | 3.25 | 5.4 | 2.66 | 2.43 | 2.06 |  | 10000 |  | 38000 | 1.21 |  | 6.1 | 2.42 |  | 1.82 | 95% | 100% | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635971 | HRCU-A-CB-O | PUZ-HA36NHA5 | PLA-A36BA* | 34000 | 12.6 | 17 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor Unit (Ceiling Cassette) | 18000 | 38000 | 40000 | 1.19 | 3.13 | 3.75 | 4.43 | 3.55 | 3.14 |  | 14000 | 28000 | 38000 | 1.38 | 3.59 | 5.3 | 2.97 | 2.28 | 2.12 |  | 9000 |  | 38000 | 0.97 |  | 5.79 | 2.71 |  | 1.92 | 95% | 100% | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Pearl Series | 8677405 | HRCU-A-CB-O | AR09KSWDHWKX | AR09KSWDHWKN | 9000 | 15.8 | 28.1 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 12600 | 12978 | 0.17 | 0.85 | 0.9 | 4.7064 | 4.3443 | 4.2261 |  | 2708 | 5600 | 13867 | 0.32 | 0.62881 | 1.79 | 2.4801 | 2.61 | 2.2704 |  | 2700 |  | 11088 | 0.38 |  | 1.81 | 2.0823 |  | 1.7953 | 85.44% | 79.96% | N/A |  |  | N/A
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Pearl Series | 8677406 | HRCU-A-CB-O | AR12KSWDHWKX | AR12KSWDHWKN | 12000 | 14.1 | 26.1 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 13600 | 14008 | 0.17 | 0.93 | 0.9765 | 4.7064 | 4.2858 | 4.2041 |  | 2726 | 7800 | 14983 | 0.32 | 0.88603 | 1.92 | 2.4966 | 2.58 | 2.287 |  | 2724 |  | 11968 | 0.37 |  | 1.92 | 2.1576 |  | 1.8268 | 85.44% | 79.88% | N/A |  |  | N/A
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | Smart Whisper Series | 8677407 | HRCU-A-CB-O | AR09KSWSJWKX | AR09KSWSJWKN | 9000 | 15 | 23 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3378 | 12000 | 12360 | 0.19 | 0.88 | 0.93 | 5.2105 | 3.9964 | 3.895 |  | 3220 | 5600 | 12612 | 0.27 | 0.62881 | 1.62 | 3.4951 | 2.61 | 2.2816 |  | 3157 |  | 10560 | 0.3 |  | 1.71 | 3.0841 |  | 1.8098 | 85.44% | 83.73% | N/A |  |  | N/A
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Whisper Series | 8677410 | HRCU-A-CB-O | AR24KSWSJWKX | AR24KSWSJWKN | 21000 | 12.5 | 21.6 | 10.7 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7506 | 27000 | 27810 | 0.48 | 2.52 | 2.646 | 4.5829 | 3.14 | 3.0802 |  | 6427 | 17000 | 28182 | 0.49 | 1.8051 | 3.84 | 3.844 | 2.76 | 2.1509 |  | 5996 |  | 23760 | 0.49 |  | 3.89 | 3.5862 |  | 1.7901 | 85.44% | 84.31% | N/A |  |  | N/A
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693477 | HMSV-A-CB | AOU48RLAVM | Non-Ducted Indoor Units | 4800 | 12.5 | 19.8 | 11.4 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 16630 | 54000 | 54000 | 0.91 | 4.06 | 4.06 | 5.3565 | 3.8981 | 3.8981 |  | 15400 | 33000 | 50000 | 1 | 3.4055 | 4.46 | 4.5134 | 2.84 | 3.2856 |  | 12720 |  | 41300 | 0.92288 |  | 4.12 | 4.0396 |  | 2.9379 | 76.48% | 82.6% | N/A |  |  | -4 | 11240 |  | 36500 | 0.86016 | 3.84 | 3.8304 | 2.7858
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693480 | HMSV-A-CB | AOU36RLAVM | Non-Ducted Indoor Units | 3600 | 13.3 | 19 | 11.4 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 16460 | 42000 | 42000 | 0.87 | 3.2 | 3.2 | 5.5462 | 3.8466 | 3.8466 |  | 16460 | 25800 | 42000 | 1.2 | 2.7005 | 4.43 | 4.021 | 2.8 | 2.7786 |  | 14860 |  | 37900 | 1.1043 |  | 4.06 | 3.9429 |  | 2.7359 | 90.24% | 90.24% | N/A |  |  | -4 | 13170 |  | 33600 | 1.02 | 3.75 | 3.7845 | 2.626
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703348 | HRCU-A-CB-O | AOU9RLS3 | ASU9RLS3Y | 9000 | 18 | 33 | 14.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 | 68.18% | 93.75% | N/A |  |  | -5 | 1945 | z | 13500 | 0.22 | 2.09 | 2.59 | 1.89
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted H Series | 8703349 | HRCU-A-CB-O | AOU9RLS3H | ASU9RLS3Y | 9000 | 18 | 33 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.33 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 | 68.18% | 93.75% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1535 | z | 11000 | 0.38 | 2.23 | 1.18 | 1.44
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703350 | HRCU-A-CB-O | AOU12RLS3 | ASU12RLS3Y | 12000 | 15.2 | 29.3 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 | 74.63% | 94.29% | N/A |  |  | -5 | 2081 | z | 15000 | 0.22 | 2.09 | 2.77 | 2.1
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8703451 | HRCU-A-CB-O | MUZ-FH12NAH | MSZ-FH12NAH | 12000 | 13.8 | 26.1 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8100 | 13600 | 0.33 | 0.84 | 1.96 | 1.87 | 2.83 | 1.96 |  | 1450 |  | 13600 | 0.28 |  | 1.93 | 1.52 |  | 2.07 | 64.76% | 100% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 550 |  | 9900 | 0.2 | 1.73 | 0.81 | 1.68
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3H Series | 8703506 | HRCU-A-CB-O | AOU12RLS3H | ASU12RLS3Y | 12000 | 15.2 | 29.3 | 13.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 | 74.63% | 94.29% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1638 | z | 11500 | 0.38 | 2.23 | 1.26 | 1.51
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703507 | HRCU-A-CB-O | AOU15RLS3 | ASU15RLS3Y | 14500 | 13.9 | 25.3 | 13.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 | 85.77% | 95.35% | N/A |  |  | -5 | 2388 | z | 18500 | 0.21 | 2.74 | 3.33 | 1.98
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703508 | HRCU-A-CB-O | AOU15RLS3H | ASU15RLS3Y | 14500 | 13.9 | 25.3 | 13.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 | 85.77% | 95.35% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2081 | z | 16000 | 0.37 | 2.88 | 1.65 | 1.63
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715783 | HRCU-A-CB-O | MUZ-GL12NA-U1 | MSZ-GL12NA-U1 | 12000 | 13 | 23.1 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2000 | 14400 | 18100 | 0.11 | 1.1 | 1.62 | 5.3286 | 3.8366 | 3.2744 |  | 1150 | 9200 | 12000 | 0.13 | 0.87 | 1.24 | 2.5926 | 3.0991 | 2.8362 |  | 1040 |  | 10200 | 0.1 |  | 1.02 | 3.0479 |  | 2.9307 | 56.35% | 76.92% | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715784 | HRCU-A-CB-O | MUZ-GL15NA-U1 | MSZ-GL15NA-U1 | 14000 | 13 | 21.6 | 11.7 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4800 | 18000 | 20900 | 0.2 | 1.6 | 2.01 | 7.0337 | 3.297 | 3.0474 |  | 2150 | 12200 | 16400 | 0.2 | 1.6 | 2.01 | 3.1505 | 2.2347 | 2.3912 |  | 2080 |  | 14100 | 0.24 |  | 1.57 | 2.5399 |  | 2.632 | 67.46% | 120% | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715785 | HRCU-A-CB-O | MUZ-GL18NA-U1 | MSZ-GL18NA-U1 | 18000 | 13.4 | 20.5 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5400 | 21600 | 25000 | 0.32 | 1.68 | 2.5 | 4.9456 | 3.7681 | 2.9307 |  | 2780 | 13800 | 18200 | 0.37 | 1.48 | 2.15 | 2.202 | 2.7327 | 2.4809 |  | 2590 |  | 15100 | 0.32 |  | 1.88 | 2.372 |  | 2.3539 | 60.4% | 86.49% | MAC-642BH-U1 | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715786 | HRCU-A-CB-O | MUZ-GL24NA-U1 | MSZ-GL24NA-U1 | 22400 | 12.5 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 27600 | 36900 | 0.52 | 2.34 | 3.65 | 4.227 | 3.4567 | 2.9628 |  | 4900 | 16000 | 24600 | 0.72 | 1.77 | 3.29 | 1.9945 | 2.6492 | 2.1914 |  | 4380 |  | 20200 | 0.64 |  | 2.99 | 2.0057 |  | 1.9799 | 54.74% | 88.89% | MAC-642BH-U1 | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Slim Duct | 8717080 | HRCU-A-CB | AC009KXADCH | AC009KNLDCH | 9000 | 13.95 | 21 | 10.5 | Yes | Ductless | Single-zone | Ducted Indoor Unit | 2900 | 12000 | 14000 | 0.25 | 1.127 | 1.5 | 3.3996 | 3.1205 | 2.7353 |  | 2720 | 7800 | 12000 | 0.31 | 0.921 | 1.54 | 2.5715 | 2.482 | 2.2837 |  | 2200 |  | 10700 | 0.34 |  | 1.62 | 1.8963 |  | 1.9357 | 76.43% | 89.17% | N/A |  |  | -4°F | 1800 |  | 8000 | 0.31 | 1.52 | 1.7017 | 1.5425
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8718495 | HRCU-A-CB-O | AOU18RLXFW1 | ASU18RLF | 18000 | 13.3 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.42 | 1.39 | 2.85 | 3.83 | 3.08 | 2.34 |  | 5205 |  | 21600 | 0.39 |  | 2.6 | 3.91 |  | 2.43 | 74.48% | 94.91% | N/A |  |  | -5 | 4745 | z | 19688 | 0.33 | 2.22 | 4.21 | 2.6
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8718545 | HRCU-A-CB-O | AOU24RLXFW1 | ASU24RLF | 22000 | 12.5 | 19.5 | 10.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.49 | 1.96 | 3.44 | 3.44 | 2.49 | 2.36 |  | 5220 |  | 25220 | 0.49 |  | 3.44 | 3.13 |  | 2.15 | 69.67% | 91.05% | N/A |  |  | -5 | 4670 |  | 22550 | 0.47 | 3.28 | 2.94 | 2.02
Electrolux Home Products | Frigidaire |  | 8718583 | HRCU-A-CB-O | FFHP093CS2 | FFHP093WS2 | 9000 | 14 | 23 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1900 | 11000 | 12000 | 0.16 | 1.02 | 1.2 | 3.4802 | 3.1606 | 2.9307 |  | 4100 | 7800 | 11000 | 0.43 | 0.83 | 1.37 | 2.7944 | 2.7542 | 2.3531 |  | 3300 |  | 10200 | 0.46 |  | 1.45 | 2.1025 |  | 2.0616 | 85% | 92.73% | Integrated | 72 | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A
Electrolux Home Products | Frigidaire |  | 8718584 | HRCU-A-CB-O | FFHP123CS2 | FFHP123WS2 | 12000 | 12.5 | 22 | 10.1 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.4 | 1.1 | 1.4 | 1.7584 | 3.4636 | 2.9307 |  | 4000 | 7500 | 11000 | 0.42 | 0.84 | 1.34 | 2.7912 | 2.6167 | 2.4058 |  | 3200 |  | 8800 | 0.45 |  | 1.27 | 2.0841 |  | 2.0307 | 62.86% | 80% | Integrated | 72±5% | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A
Electrolux Home Products | Frigidaire |  | 8718585 | HRCU-A-CB-O | FFHP183CS2 | FFHP183WS2 | 18000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7340 | 8806.37 | 19315.3 | 0.58 | 0.633 | 2.468 | 3.7089 | 4.0772 | 2.2937 |  | 7120 | 12470.86 | 18687.5 | 0.61 | 1.37 | 2.613 | 3.4208 | 2.6678 | 2.096 |  | 6870 |  | 16425.3 | 0.63 |  | 2.622 | 3.1959 |  | 1.8359 | 85.04% | 87.89% | Integrated | 160±5% | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8737963 | HRCU-A-CB-O | MUZ-FH09NAH | MSZ-FH09NAH | 9000 | 16.1 | 30.5 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 10900 | 18000 | 0.11 | 0.55 | 1.27 | 4.263 | 5.86 | 4.15 |  | 920 | 6700 | 12200 | 0.34 | 0.72 | 1.26 | 0.79 | 2.73 | 2.84 |  | 640 |  | 10900 | 0.32 |  | 1.17 | 0.59 |  | 2.73 | 60.56% | 89.34% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 240 |  | 7300 | 0.29 | 1.06 | 0.24 | 2.02
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737964 | HRCU-A-CB-O | MUZ-FH15NAH | MSZ-FH15NA | 15000 | 12.5 | 22 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 4280 | 18540 | 24200 | 0.61 | 1.33 | 3.4 | 2.0564 | 4.0854 | 2.086 | 3570 | 3570 | 11070 | 20200 | 0.6 | 0.95 | 3.36 | 1.7438 | 3.415 | 1.7619 |  | 3240 | 8550 | 18300 | 0.55 | 0.74 | 2.98 | 1.7265 | 3.3862 | 1.7997 | 75.62% | 91.67% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 2610 |  | 14700 | 0.56 | 2.54 | 1.3659 | 1.6961
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737968 | HRCU-A-CB-O | MUZ-FE09NAH | MSZ-FE09NA | 9000 | 15.5 | 26 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8614 | 4.4993 | 2.3446 | 1840 | 1840 | 6700 | 13700 | 0.26 | 0.67 | 1.89 | 2.074 | 2.9307 | 2.1244 |  | 1430 | 11200 | 11200 | 0.25 | 1.59 | 1.59 | 1.6764 | 2.0644 | 2.7709 | 62.22% | 81.75% | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737969 | HRCU-A-CB-O | MUZ-FE12NAH | MSZ-FE12NA | 12000 | 12.9 | 23 | 10.1 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8614 | 4.1955 | 2.7353 | 1840 | 1840 | 8400 | 15100 | 0.26 | 0.84 | 1.89 | 2.074 | 2.9307 | 2.3415 |  | 1430 | 6500 | 12500 | 0.25 | 0.68 | 1.59 | 1.6764 | 2.8014 | 2.304 | 59.52% | 96.15% | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Carrier | Carrier |  | 8738635 | HRCU-A-CB-O | 38MAQB09R--3 | 40MAQB09B--3 | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 |  | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.5585 | 2.74 | 2.26 |  | 1907 |  | 10900 | 0.13 |  | 1.613 | 4.3 |  | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier |  | 8738636 | HRCU-A-CB-O | 38MAQB12R--3 | 40MAQB12B--3 | 12000 | 12.5 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 |  | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.412 | 2.64 | 2.26 |  | 2030 |  | 12010 | 0.141 |  | 1.78 | 4.22 |  | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier |  | 8738638 | HRCU-A-CB-O | 38MAQB24R--3 | 40MAQB24B--3 | 24000 | 13 | 20.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 |  | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.4435 | 2.64 | 1.95 |  | 2856 |  | 24030 | 0.295 |  | 3.98 | 2.83 |  | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | Preferred Series | 8738643 | HRCU-A-CB-O | 38MAQB24R--3 | 619PEQ024BBMA | 24000 | 13 | 20.5 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 |  | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.42 | 2.64 | 1.95 |  | 2856 |  | 24030 | 0.295 |  | 3.98 | 2.83 |  | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | Preferred Series | 8738645 | HRCU-A-CB-O | 38MAQB12R--3 | 619PEQ012BBMA | 12000 | 12.5 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 |  | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.412 | 2.64 | 2.26 |  | 2030 |  | 12010 | 0.141 |  | 1.78 | 4.22 |  | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Bryant | Preferred Series | 8738646 | HRCU-A-CB-O | 38MAQB09R--3 | 619PEQ009BBMA | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 |  | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.5585 | 2.74 | 2.26 |  | 1907 |  | 10900 | 0.13 |  | 1.613 | 4.3 |  | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
American Standard | American Standard | AccuComfort Platinum 20 | 8759144 | HRCU-A-CB | 4A6V0036A1 | *UD2C080ACV4 & 4PXCCU48BS3 | 36800 | 13 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33300 | 0.52 | 2.42 | 2.41 | 4.78 | 4.0196 | 4.04 |  | 15930 | 26600 | 26700 | 1.84 | 2.42 | 3.24 | 2.54 | 3.2205 | 2.42 |  | 16688 |  | 20220 | 2.62 |  | 3.1 | 1.86 |  | 1.90 | 60.72% | 75.73% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 8759145 | HRCU-A-CB | 4A6V0036A1 | *UD2C100ACV5 & 4PXCCU48BS3 | 37000 | 13 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33200 | 33300 | 0.51 | 2.44 | 2.37 | 4.82 | 3.9867 | 4.12 |  | 15710 | 26600 | 26600 | 1.81 | 2.44 | 3.2 | 2.54 | 3.1942 | 2.44 |  | 16488 |  | 20080 | 2.58 |  | 3.06 | 1.88 |  | 1.90 | 60.3% | 75.49% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8759184 | HRCU-A-CB | 4A6V8036A1 | *UD2C100ACV5 & 4PXCCU36BS3 | 35000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 32100 | 0.5 | 2.34 | 2.46 | 4.86 | 3.9818 | 3.82 |  | 16040 | 26000 | 26200 | 1.83 | 2.34 | 3.29 | 2.56 | 3.2555 | 2.34 |  | 16934 |  | 20300 | 2.6 |  | 3.14 | 1.90 |  | 1.90 | 63.24% | 77.48% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8759191 | HRCU-A-CB | 4A6V8036A1 | *UD2C100ACV5 & 4PXCCU48BS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16040 | 26200 | 26400 | 1.79 | 2.44 | 3.17 | 2.62 | 3.1461 | 2.44 |  | 16894 |  | 20300 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 61.89% | 76.89% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8759192 | HRCU-A-CB | 4A6V8036A1 | *UD2B100ACV3 & 4PXCCU60BS3 | 36600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32400 | 32500 | 0.5 | 2.4 | 2.39 | 4.86 | 3.9555 | 3.98 |  | 16480 | 26400 | 26500 | 1.83 | 2.4 | 3.23 | 2.64 | 3.223 | 2.4 |  | 17440 |  | 20740 | 2.62 |  | 3.1 | 1.96 |  | 1.95 | 63.82% | 78.26% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8759235 | HRCU-A-CB | 4A6V8048A1 | *UD2D120ACV5 & 4PXCDU60BS3 | 48000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12300 | 44000 | 44600 | 0.78 | 2.4 | 3.4 | 4.62 | 5.3716 | 3.84 |  | 23510 | 37000 | 37400 | 2.56 | 2.4 | 4.56 | 2.7 | 4.517 | 2.4 |  | 24696 |  | 29340 | 3.62 |  | 4.34 | 2.00 |  | 2.00 | 65.78% | 78.45% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761163 | HRCU-A-CB | 4A6V8036A1 | *UD2B080ACV3 & 4TXCB006DS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 33000 | 0.51 | 2.4 | 2.42 | 4.82 | 4.0043 | 4 |  | 16590 | 26600 | 26800 | 1.87 | 2.4 | 3.28 | 2.6 | 3.2474 | 2.4 |  | 17540 |  | 20900 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.33% | 77.99% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761164 | HRCU-A-CB | 4A6V8036A1 | *UD2B060ACV3 & 4TXCB006DS3 | 36000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 33000 | 0.52 | 2.4 | 2.43 | 4.74 | 4.0043 | 3.98 |  | 16590 | 26600 | 26800 | 1.86 | 2.4 | 3.28 | 2.62 | 3.2474 | 2.4 |  | 17540 |  | 20900 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.33% | 77.99% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761165 | HRCU-A-CB | 4A6V8036A1 | *UD2C080ACV4 & 4TXCC005DS3 | 35200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 32200 | 0.51 | 2.34 | 2.46 | 4.82 | 4.0068 | 3.84 |  | 16150 | 26200 | 26300 | 1.83 | 2.34 | 3.3 | 2.58 | 3.2806 | 2.34 |  | 17094 |  | 20400 | 2.62 |  | 3.14 | 1.92 |  | 1.90 | 63.35% | 77.57% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761167 | HRCU-A-CB | 4A6V8036A1 | *UD2C100ACV5 & 4TXCC005DS3 | 35000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 32100 | 0.5 | 2.34 | 2.46 | 4.86 | 3.9818 | 3.82 |  | 16040 | 26000 | 26200 | 1.83 | 2.34 | 3.29 | 2.56 | 3.2555 | 2.34 |  | 16934 |  | 20300 | 2.6 |  | 3.14 | 1.90 |  | 1.90 | 63.24% | 77.48% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761170 | HRCU-A-CB | 4A6V8036A1 | *UD2B100ACV3 & 4TXCC007DS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33000 | 33000 | 0.51 | 2.42 | 2.42 | 4.82 | 3.9954 | 4 |  | 16590 | 26800 | 26900 | 1.86 | 2.42 | 3.27 | 2.62 | 3.2448 | 2.42 |  | 17640 |  | 21000 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.64% | 78.07% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761171 | HRCU-A-CB | 4A6V8036A1 | *UD2C080ACV4 & 4TXCC007DS3 | 36400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16150 | 26400 | 26500 | 1.8 | 2.44 | 3.18 | 2.62 | 3.1701 | 2.44 |  | 16994 |  | 20400 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 62.2% | 76.98% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761172 | HRCU-A-CB | 4A6V8036A1 | *UHMB080ACV3 & 4TXCC007DS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33000 | 33100 | 0.56 | 2.4 | 2.44 | 4.44 | 4.0287 | 3.98 |  | 16700 | 26800 | 26900 | 1.89 | 2.4 | 3.28 | 2.58 | 3.2718 | 2.4 |  | 17640 |  | 21040 | 2.68 |  | 3.16 | 1.92 |  | 1.95 | 63.56% | 78.22% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761173 | HRCU-A-CB | 4A6V8036A1 | *UD2C100ACV5 & 4TXCC007DS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16040 | 26200 | 26400 | 1.79 | 2.44 | 3.17 | 2.62 | 3.1461 | 2.44 |  | 16894 |  | 20300 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 61.89% | 76.89% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761175 | HRCU-A-CB | 4A6V8036A1 | *UHMC100ACV4 & 4TXCC007DS3 | 36400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 32900 | 0.53 | 2.46 | 2.35 | 4.64 | 3.9066 | 4.1 |  | 16370 | 26600 | 26700 | 1.81 | 2.46 | 3.18 | 2.64 | 3.1682 | 2.46 |  | 17194 |  | 20600 | 2.56 |  | 3.04 | 1.96 |  | 2.00 | 62.61% | 77.15% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761183 | HRCU-A-CB | 4A6V8037A1 | *UD2B080ACV3 & 4TXCB006DS3 | 36600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33500 | 0.53 | 2.36 | 2.48 | 4.7 | 4.1218 | 3.96 |  | 16370 | 26800 | 27000 | 1.91 | 2.36 | 3.34 | 2.52 | 3.3273 | 2.36 |  | 17340 |  | 20760 | 2.72 |  | 3.22 | 1.86 |  | 1.90 | 61.97% | 76.89% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761190 | HRCU-A-CB | 4A6V8037A1 | *UHMC100ACV4 & 4TXCC007DS3 | 36800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761191 | HRCU-A-CB | 4A6V8037A1 | *UD2C100ACV5 & 4TXCC007DS3 | 37000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33200 | 33300 | 0.51 | 2.44 | 2.37 | 4.82 | 3.9867 | 4.12 |  | 15710 | 26600 | 26600 | 1.81 | 2.44 | 3.2 | 2.54 | 3.1942 | 2.44 |  | 16488 |  | 20080 | 2.58 |  | 3.06 | 1.88 |  | 1.90 | 60.3% | 75.49% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761192 | HRCU-A-CB | 4A6V8037A1 | *UD2C080ACV4 & 4TXCC007DS3 | 36800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33300 | 0.52 | 2.42 | 2.41 | 4.78 | 4.0196 | 4.04 |  | 15930 | 26600 | 26700 | 1.84 | 2.42 | 3.24 | 2.54 | 3.2205 | 2.42 |  | 16688 |  | 20220 | 2.62 |  | 3.1 | 1.86 |  | 1.90 | 60.72% | 75.73% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761198 | HRCU-A-CB | 4A6V8048A1 | *UD2D120ACV5 & 4TXCC009DS3 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44700 | 0.82 | 2.36 | 3.56 | 4.44 | 5.4006 | 3.68 |  | 23400 | 36600 | 37600 | 2.64 | 2.36 | 4.67 | 2.6 | 4.5439 | 2.36 |  | 24496 |  | 29200 | 3.72 |  | 4.44 | 1.92 |  | 1.95 | 65.32% | 77.66% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761199 | HRCU-A-CB | 4A6V8048A1 | *UD2C080ACV4 & 4TXCC009DS3 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44700 | 0.83 | 2.34 | 3.59 | 4.38 | 5.4467 | 3.64 |  | 23180 | 36400 | 37400 | 2.65 | 2.34 | 4.7 | 2.56 | 4.5577 | 2.34 |  | 24250 |  | 28900 | 3.72 |  | 4.46 | 1.90 |  | 1.90 | 64.65% | 77.27% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761201 | HRCU-A-CB | 4A6V8048A1 | *UHMC100ACV4 & 4TXCC009DS3 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44800 | 0.85 | 2.36 | 3.57 | 4.28 | 5.4006 | 3.68 |  | 23400 | 36600 | 37500 | 2.66 | 2.36 | 4.67 | 2.58 | 4.5439 | 2.36 |  | 24456 |  | 29140 | 3.72 |  | 4.44 | 1.92 |  | 1.90 | 65.04% | 77.71% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761202 | HRCU-A-CB | 4A6V8048A1 | *UD2C100ACV5 & 4TXCC009DS3 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12300 | 43500 | 44600 | 0.82 | 2.38 | 3.51 | 4.4 | 5.3552 | 3.72 |  | 23290 | 36600 | 37400 | 2.61 | 2.38 | 4.62 | 2.62 | 4.5058 | 2.38 |  | 24456 |  | 29140 | 3.66 |  | 4.38 | 1.96 |  | 1.95 | 65.34% | 77.91% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 8761205 | HRCU-A-CB | 4A6V8048A1 | *UD2D120ACV5 & 4TXCD010DS3 | 48000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12300 | 44000 | 44600 | 0.78 | 2.4 | 3.4 | 4.62 | 5.3716 | 3.84 |  | 23510 | 37000 | 37400 | 2.56 | 2.4 | 4.56 | 2.7 | 4.517 | 2.4 |  | 24696 |  | 29340 | 3.62 |  | 4.34 | 2.00 |  | 2.00 | 65.78% | 78.45% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 8761409 | HRCU-A-CB | 4TWV0036A1 | *UHMB060ACV3 & 4TXCB006DS3 | 35400 | 13 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 8700 | 32800 | 33700 | 0.61 | 2.28 | 2.65 | 4.18 | 4.215 | 3.72 |  | 16260 | 26400 | 27100 | 1.99 | 2.28 | 3.49 | 2.4 | 3.3926 | 2.28 |  | 16994 |  | 20520 | 2.8 |  | 3.34 | 1.78 |  | 1.80 | 60.89% | 75.72% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 8761420 | HRCU-A-CB | 4TWV0036A1 | *UHMC100ACV4 & 4TXCC007DS3 | 36800 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 8761470 | HRCU-A-CB | 4TWV8036A1 | *UHMB080ACV3 & 4TXCC007DS3 | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33000 | 33100 | 0.56 | 2.4 | 2.44 | 4.44 | 4.0287 | 3.98 |  | 16700 | 26800 | 26900 | 1.89 | 2.4 | 3.28 | 2.58 | 3.2718 | 2.4 |  | 17640 |  | 21040 | 2.68 |  | 3.16 | 1.92 |  | 1.95 | 63.56% | 78.22% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 8761473 | HRCU-A-CB | 4TWV8036A1 | *UHMC100ACV4 & 4TXCC007DS3 | 36400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 32900 | 0.53 | 2.46 | 2.35 | 4.64 | 3.9066 | 4.1 |  | 16370 | 26600 | 26700 | 1.81 | 2.46 | 3.18 | 2.64 | 3.1682 | 2.46 |  | 17194 |  | 20600 | 2.56 |  | 3.04 | 1.96 |  | 2.00 | 62.61% | 77.15% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 8761492 | HRCU-A-CB | 4TWV8037A1 | *UHMC100ACV4 & 4TXCC007DS3 | 36800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 8761505 | HRCU-A-CB | 4TWV8048A1 | *UHMC100ACV4 & 4TXCC009DS3 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44800 | 0.85 | 2.36 | 3.57 | 4.28 | 5.4006 | 3.68 |  | 23400 | 36600 | 37500 | 2.66 | 2.36 | 4.67 | 2.58 | 4.5439 | 2.36 |  | 24456 |  | 29140 | 3.72 |  | 4.44 | 1.92 |  | 1.90 | 65.04% | 77.71% | N/A |  |  | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775829 | HRCU-A-CB-O | MOD30-24HFN1-MT0W | CS11M-23HRFN1-MT0W | 24000 | 13 | 20.5 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7255 | 24000 | 30235 | 0.451 | 1.954 | 3.17 | 4.7145 | 3.5996 | 2.7953 |  | 5813 | 15400 | 26330 | 0.541 | 1.635 | 4.18 | 3.149 | 2.7604 | 1.8461 |  | 5078 |  | 26026 | 0.487 |  | 4.29 | 3.0559 |  | 1.778 | 86.08% | 98.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775842 | HRCU-A-CB-O | MOBA30-09HFN1-MT0W | CCA3U-09HRFN1-M(C) | 9000 | 13 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775845 | HRCU-A-CB-O | MOB30-12HFN1-MT0W | CCA3U-12HRFN1-M(C) | 12000 | 14 | 21.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 13353 | 0.181 | 0.902 | 1.09 | 6.2873 | 3.8989 | 3.5903 |  | 3086 | 7500 | 9902 | 0.219 | 0.82 | 1.33 | 4.1298 | 2.6805 | 2.1819 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 63.37% | 85.46% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775849 | HRCU-A-CB-O | MOCA31-18HFN1-MT0W | CCA3U-18HRFN1-M(C) | 18000 | 12.5 | 20 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 19358 | 0.244 | 1.499 | 1.68 | 5.8794 | 3.5192 | 3.3769 |  | 3931 | 12000 | 13936 | 0.282 | 1.274 | 1.55 | 4.0853 | 2.7605 | 2.635 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 48.61% | 67.52% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775850 | HRCU-A-CB-O | MOCA31-18HFN1-MT0W | MUEU-18HRFN1-M(C) | 18000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4826 | 18000 | 19020 | 0.238 | 1.552 | 1.65 | 5.9427 | 3.399 | 3.3783 |  | 3964 | 12000 | 13823 | 0.282 | 1.303 | 1.531 | 4.1196 | 2.699 | 2.6461 |  | 3423 |  | 10274 | 0.253 |  | 1.433 | 3.9651 |  | 2.1012 | 54.02% | 74.33% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775852 | HRCU-A-CB-O | MOD31-24HFN1-MT0W | MCDU-24HRFN1-M(C) | 24000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 30246 | 0.448 | 2.043 | 2.65 | 4.6119 | 3.5002 | 3.345 |  | 5712 | 15800 | 19158 | 0.541 | 1.809 | 2.58 | 3.0943 | 2.5597 | 2.1762 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 50.67% | 80% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775853 | HRCU-A-CB-O | MOD31-24HFN1-MT0W | MUEU-24HRFN1-M(C) | 24000 | 12.5 | 20 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 29873 | 0.448 | 1.733 | 2.69 | 4.5805 | 4.0587 | 3.2546 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 59.27% | 97.21% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8779045 | HRCU-A-CB-O | AOU18RLXFWH | ASU18RLF | 18000 | 13.3 | 20 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.57 | 1.42 | 3 | 2.82 | 3.02 | 2.22 |  | 5205 |  | 21600 | 0.54 |  | 2.75 | 2.82 |  | 2.3 | 74.48% | 94.91% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 4317 | z | 17913 | 0.42 | 1.83 | 3.01 | 2.87
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8779046 | HRCU-A-CB-O | AOU24RLXFWH | ASU24RLF | 22000 | 12.5 | 19.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.64 | 2.11 | 3.59 | 2.63 | 2.32 | 2.26 |  | 5220 |  | 25220 | 0.64 |  | 3.59 | 2.4 |  | 2.06 | 69.67% | 91.05% | Integrated | 0.15 | Cold outside & demand | -15 | 7510 |  | 19720 | 0.5 | 3.22 | 4.4 | 1.8
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779089 | HRCU-A-CB-O | A-VMH24SU-1 | B-VMH24SU-1 | 24000 | 13 | 20.5 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.0298 | 3.5999 | 2.7199 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.7599 | 2.7599 | 1.9499 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.7799 |  | 1.8099 | 82.85% | 95.64% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779091 | HRCU-A-CB-O | B-VMH12SU-1 | A-VMH12SU-1 | 12000 | 13 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.2998 | 3.5399 | 3.2699 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.6399 | 2.6399 | 2.2099 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779092 | HRCU-A-CB-O | A-VMH09SU-1 | B-VMH09SU-1 | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8797130 | HRCU-A-CB-O | MUZ-FH06NA | MSZ-FH06NA | 6000 | 19 | 33.1 | 13.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.08 | 0.5 | 1 | 3.37 | 3.46 | 3.13 |  | 640 |  | 8700 | 0.06 |  | 0.91 | 3.13 |  | 2.8 | 62.14% | 81.31% | Accessory (MAC-640BH-U) | 106W @208V; 130W @230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 |  | 6400 | 0.03 | 0.8 | 2.34 | 2.34
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8797132 | HRCU-A-CB-O | MUZ-FH06NAH | MSZ-FH06NAH | 6000 | 19 | 33.1 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.21 | 0.628 | 1.13 | 1.28 | 2.75 | 2.78 |  | 640 |  | 8700 | 0.19 |  | 1.04 | 0.99 |  | 2.45 | 62.14% | 81.31% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 240 |  | 2100 | 0.16 | 0.93 | 0.44 | 2.02
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8797133 | HRCU-A-CB-O | MUZ-FH18NA2 | MSZ-FH18NA2 | 17200 | 12.5 | 21 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5150 | 20300 | 30000 | 0.43 | 1.72 | 3.39 | 3.51 | 3.46 | 2.59 |  | 2950 | 13700 | 20300 | 0.31 | 1.32 | 2.8 | 2.79 | 3.04 | 2.12 |  | 2050 |  | 20300 | 0.23 |  | 2.96 | 2.61 |  | 2.01 | 67.67% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 |  | 14000 | 0.11 | 2.35 | 2 | 1.74
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8797134 | HRCU-A-CB-O | MUZ-FH18NAH2 | MSZ-FH18NA | 17200 | 12.5 | 21 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 7540 | 20300 | 30400 | 0.85 | 1.77 | 3.4 | 2.5997 | 3.3612 | 2.6204 | 4300 | 4300 | 12480 | 24300 | 0.6 | 1.25 | 3.39 | 2.1003 | 2.926 | 2.1008 |  | 3700 | 9640 | 20900 | 0.53 | 0.98 | 2.98 | 2.046 | 2.8829 | 2.0554 | 68.75% | 88.33% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 2640 |  | 14900 | 0.54 | 2.46 | 1.4328 | 1.7751
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849330 | HRCU-A-CB-O | RXL15QMVJU | FTX15NMVJU | 15000 | 13 | 20 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5814 | 18295 | 24566 | 0.39 | 1.341 | 2.307 | 4.37 | 4 | 3.12 |  | 3784 | 11904 | 19755 | 0.341 | 1.17 | 2.361 | 3.25 | 2.98 | 2.45 |  | 2958 |  | 18254 | 0.32 |  | 2.361 | 2.71 |  | 2.27 | 74.31% | 92.4% | N/A |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849445 | HRCU-A-CB-O | RXL15QMVJU | FVXS15NVJU | 15000 | 12.5 | 20 | 11.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5814 | 18056 | 23884 | 0.34 | 1.401 | 1.809 | 5.01 | 3.78 | 3.87 |  | 3784 | 11751 | 19414 | 0.297 | 1.222 | 2.105 | 3.73 | 2.82 | 2.7 |  | 2958 |  | 18015 | 0.279 |  | 2.198 | 3.11 |  | 2.4 | 75.43% | 92.79% | N/A |  |  | N/A |  | z
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series; KJ-Series | 8849446 | HRCU-A-CB-O | MUFZ-KJ12NAHZ | MFZ-KJ12NA | 12000 | 13.6 | 25.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2900 | 13000 | 22800 | 0.27 | 0.9 | 2.39 | 3.15 | 4.23 | 2.8 |  | 1650 | 8800 | 14800 | 0.2 | 0.93 | 1.89 | 2.42 | 2.77 | 2.29 |  | 1150 |  | 13000 | 0.15 |  | 1.81 | 2.25 |  | 2.1 | 57.02% | 87.84% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 |  | 8000 | 0.07 | 1.28 | 1.76 | 1.83
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849458 | HRCU-A-CB-O | RXL12QMVJU | FTX12NMVJU | 10900 | 12.5 | 20 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 13679 | 18766 | 0.24 | 1.026 | 1.562 | 5.43 | 3.91 | 3.52 |  | 2893 | 8902 | 15388 | 0.21 | 0.895 | 1.789 | 4.04 | 2.92 | 2.52 |  | 2262 |  | 14330 | 0.197 |  | 1.86 | 3.37 |  | 2.26 | 76.36% | 93.12% | N/A |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849459 | HRCU-A-CB-O | RXL09QMVJU | FVXS09NVJU | 9000 | 12.5 | 20 | 11.7 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 10089 | 14330 | 0.24 | 0.721 | 1.356 | 5.43 | 4.1 | 3.1 |  | 2893 | 6565 | 11082 | 0.21 | 0.629 | 1.378 | 4.04 | 3.06 | 2.36 |  | 2262 |  | 10065 | 0.197 |  | 1.384 | 3.37 |  | 2.13 | 70.24% | 90.82% | N/A |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849533 | HRCU-A-CB-O | RXL09QMVJU | FTX09NMVJU | 9000 | 12.5 | 20 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 10942 | 16036 | 0.23 | 0.761 | 1.701 | 5.67 | 4.21 | 2.76 |  | 2893 | 7121 | 12136 | 0.201 | 0.664 | 1.642 | 4.22 | 3.14 | 2.17 |  | 2262 |  | 10918 | 0.189 |  | 1.623 | 3.51 |  | 1.97 | 68.08% | 89.96% | N/A |  |  | N/A |  | z
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849535 | HMSV-A-CB | 2MXL18QMVJU | 40GRQB18H--301 | 18000 | 12.7 | 17 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7710 | 18940 | 36000 | 0.47 | 1.32 | 3.17 | 4.81 | 4.21 | 3.33 |  | 5020 | 12330 | 23480 | 0.41 | 1.15 | 2.77 | 3.5885 | 3.14 | 2.48 |  | 4050 |  | 18930 | 0.39 |  | 2.62 | 3.04 |  | 2.12 | 52.58% | 80.62% | N/A |  |  | N/A
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849539 | HMSV-A-CB | 3MXL24QMVJU | CTXS07LVJU+FTXS09LVJU+FTXS09LVJU | 24000 | 12.7 | 17.9 | 12.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7720 | 24000 | 41000 | 0.44 | 1.54 | 3.52 | 5.14 | 4.57 | 3.41 |  | 5030 | 15670 | 26780 | 0.38 | 1.35 | 3.08 | 3.8795 | 3.4 | 2.55 |  | 4060 |  | 21600 | 0.36 |  | 2.92 | 3.31 |  | 2.17 | 52.68% | 80.66% | N/A |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854557 | HRCU-A-CB-O | MUFZ-KJ09NAHZ | MFZ-KJ09NA | 9000 | 15.8 | 28.2 | 13 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2900 | 11000 | 19000 | 0.27 | 0.75 | 2.37 | 3.15 | 4.3 | 2.35 |  | 1650 | 7500 | 13400 | 0.2 | 0.8 | 1.86 | 2.42 | 2.75 | 2.11 |  | 1150 |  | 11000 | 0.15 |  | 1.6 | 2.25 |  | 2.01 | 57.89% | 82.09% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 |  | 7000 | 0.07 | 1.27 | 1.76 | 1.62
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8854558 | HRCU-A-CB-O | MUFZ-KJ15NAHZ | MFZ-KJ15NA | 15000 | 13.5 | 21.8 | 11.6 | Yes | Ductless | Single-zone | Non-ducted indoor units (Floor Mount) | 5100 | 18000 | 25000 | 0.7 | 1.41 | 3.41 | 2.1352 | 3.7413 | 2.1486 | 3540 | 3540 | 14400 | 20000 | 0.44 | 1.19 | 3.04 | 2.3579 | 3.5464 | 1.9281 |  | 3190 |  | 18000 | 0.4 |  | 2.83 | 2.3372 |  | 1.8641 | 72% | 90.91% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854559 | HRCU-A-CB-O | MUFZ-KJ18NAHZ | MFZ-KJ18NA | 17000 | 12.6 | 21 | 11.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5700 | 21000 | 29000 | 0.48 | 1.73 | 3.43 | 3.48 | 3.56 | 2.48 |  | 3250 | 12800 | 23000 | 0.35 | 1.43 | 3.21 | 2.72 | 2.62 | 2.1 |  | 2260 |  | 21000 | 0.26 |  | 3 | 2.55 |  | 2.05 | 72.41% | 91.3% | Integrated | 98W @208V; 120W @ 230 V |  | -13 | 840 |  | 15700 | 0.13 | 2.3 | 1.89 | 2
Carrier | Bryant | Preferred Series | 8856652 | HRCU-A-CB | 38MAQB18R--3 | 619REQ018DBMA | 16500 | 12.5 | 19.6 | 10.5 | Yes | Ductless | Single-zone | Ducted Indoor Units | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 |  | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 |  | 5500 |  | 18000 | 0.67729 |  | 3.0146 | 2.38 |  | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier |  | 8856653 | HRCU-A-CB | 38MAQB18R--3 | 40MBQB18D--3 | 16500 | 12.5 | 19.6 | 10.5 | Yes | Ductless | Single-zone | Ducted Indoor Units | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 |  | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 |  | 5500 |  | 18000 | 0.67729 |  | 3.0146 | 2.38 |  | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | Preferred Series | 8856654 | HRCU-A-CB-O | 38MAQB18R--3 | 619REQ018CBMA | 16000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Carrier | Carrier |  | 8856655 | HRCU-A-CB-O | 38MAQB18R--3 | 40MBQB18C--3 | 16000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
Panasonic | Panasonic | Exterios XE | 8860533 | HRCU-A-CB-O | CU-XE9SKUA | CS-XE9SKUA | 8700 | 17.05 | 30.6 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10900 | 18000 | 0.15 | 0.67 | 1.65 | 5.93 | 4.78 | 3.21 |  | 2100 | 8000 | 11000 | 0.14 | 0.75 | 1.38 | 4.3988 | 3.1261 | 2.34 |  | 1700 |  | 11000 | 0.12 |  | 1.73 | 4.1544 |  | 1.86 | 61.11% | 100% | included with outdoor unit CU-XE9SKUA | 510 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 10400 | 0.1 | 1.72 | 3.8123 | 1.7732
Panasonic | Panasonic | Exterios XE | 8861565 | HRCU-A-CB-O | CU-XE12SKUA | CS-XE12SKUA | 11500 | 14.7 | 26.2 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13600 | 23000 | 0.15 | 0.95 | 2.1 | 5.93 | 4.1955 | 3.2 |  | 2100 | 10400 | 12500 | 0.14 | 1.05 | 1.6662 | 4.3988 | 2.9028 | 2.2 |  | 1700 |  | 12500 | 0.12 |  | 1.99 | 4.1544 |  | 1.84 | 54.35% | 100% | included with outdoor unit CU-XE12SKUA | 780 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 11800 | 0.1 | 2.01 | 3.8123 | 1.7216
Haier | Haier | Arctic Series | 8862047 | HRCU-A-CB-O | 1U09EH2VHA | AW09EH2VHA | 9000 | 15.5 | 28 | 13 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 12000 | 22000 | 0.245 | 0.9 | 1.65 | 4.785 | 3.9078 | 3.908 |  | 3100 | 9000 | 12000 | 0.26 | 0.82 | 1.18 | 3.494 | 3.217 | 2.981 |  | 2800 |  | 12000 | 0.26 |  | 1.58 | 3.156 |  | 2.226 | 54.55% | 100% | Integrated | 300 | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
Haier | Haier | Arctic Series | 8862052 | HRCU-A-CB-O | 1U12EH2VHA | AW12EH2VHA | 12000 | 13 | 25 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 16500 | 22200 | 0.225 | 1.345 | 1.69 | 5.341 | 3.5954 | 3.85 |  | 3200 | 10000 | 16500 | 0.33 | 1.185 | 1.595 | 2.842 | 2.473 | 3.032 |  | 2900 |  | 16500 | 0.3 |  | 2.152 | 2.833 |  | 2.247 | 74.32% | 100% | Integrated | 300 | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
Haier | Haier | Arctic Series | 8862057 | HRCU-A-CB-O | 1U18EH2VHA | AW18EH2VHA | 19000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 20400 | 26400 | 0.55 | 1.64 | 3.1 | 3.624 | 3.6457 | 2.496 |  | 5800 | 18500 | 20400 | 0.58 | 1.9 | 2.95 | 2.931 | 2.854 | 2.027 |  | 4700 |  | 20400 | 0.55 |  | 3.15 | 2.505 |  | 1.898 | 77.27% | 100% | Integrated | 300 | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z
Lennox Industries, Inc. | Lennox | ML-Series | 8898932 | N/A | MLA009S4S-1P | MWMA009S4-1P |  | 14.5 | 24 | 10.5 | Yes | Ductless | Single-zone | N/A | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | ML-Series | 8898934 | N/A | MLA012S4S-1P | MMDA012S4-1P |  | 12.5 | 19 | 10 | Yes | Ductless | Single-zone | N/A | 3752 | 12000 | 17021 | 0.189 | 0.961 | 1.692 | 5.818 | 3.6596 | 2.9482 |  | 3292 | 8500 | 12986 | 0.232 | 0.966 | 2.028 | 4.1586 | 2.5788 | 1.8766 |  | 2718 |  | 12341 | 0.205 |  | 2.031 | 3.8857 |  | 1.7808 | 72.5% | 95.03% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | ML-Series | 8898935 | N/A | MLA012S4S-1P | MWMA012S4-1P |  | 12.5 | 22 | 10 | Yes | Ductless | Single-zone | N/A | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | ML-Series | 8898941 | N/A | MLA024S4S-1P | MWMA024S4-1P |  | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | N/A | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8908615 | HMSV-A-CB | AOU36RLXFZH | Non-Ducted Indoor Units | 35200 | 13 | 20 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 12000 | 36400 | 42000 | 0.7 | 2.67 | 3.29 | 5.02 | 4 | 3.74 |  | 11212 | 21400 | 39341 | 1.09 | 2.38 | 5.13 | 3.02 | 2.64 | 2.25 |  | 10376 |  | 36407 | 1.12 |  | 5.28 | 2.72 |  | 2.02 | 86.68% | 92.54% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 6301 | z | 22110 | 0.91 | 3.59 | 2.03 | 1.81
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8912454 | HRCU-A-CB-O | AOU30RLXEH | ASU30RLE | 30000 | 12.5 | 18.7 | 11.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 8000 | 22600 | 37200 | 0.5 | 2.4 | 2.54 | 4.7 | 2.77 | 2.54 |  | 7570 | 21400 | 35200 | 0.53 | 2.52 | 4.51 | 4.2 | 2.49 | 2.29 |  | 6890 |  | 32040 | 0.53 |  | 4.55 | 3.79 |  | 2.06 | 86.13% | 91.02% | Integrated | 0.15 | Cold outside & demand | -15 | 4620 |  | 22860 | 0.46 | 3.95 | 3.12 | 1.7
Friedrich Air Conditioning | Friedrich | J-Series | 8915232 | HMSV-A-CB | MR24DY3JMA | Non-Ducted | 20000 | 13.5 | 21.7 | 10.6 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 24000 | 28800 | 1.092 | 1.8 | 2.52 | 2.4798 | 3.9076 | 3.3494 |  | 5580 | 14500 | 21097 | 0.945 | 1.56 | 1.71 | 1.7305 | 2.7241 | 3.6157 |  | 4332 |  | 14595 | 0.917 |  | 1.65 | 1.3845 |  | 2.5923 | 50.68% | 69.18% | N/A |  |  | N/A
Friedrich Air Conditioning | Friedrich | J-Series | 8915234 | HMSV-A-CB | MR24DY3JMA | Mixed | 18900 | 12.5 | 19.6 | 10.2 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 10230 | 23250 | 27900 | 1.171 | 1.859 | 2.6 | 2.5603 | 3.6654 | 3.1449 |  | 6270 | 14250 | 20394 | 1.008 | 1.61 | 1.76 | 1.823 | 2.594 | 3.396 |  | 4932 |  | 14109 | 0.973 |  | 1.7 | 1.4855 |  | 2.4323 | 50.57% | 69.18% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 8935197 | HRCU-A-CB | 4A6V0024A1 | *DD2B060ACV3 & 4PXCBD36BS3 | 24400 | 13.5 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22000 | 0.53 | 2.54 | 1.57 | 4.48 | 2.5608 | 4.1 |  | 11540 | 17200 | 17100 | 1.22 | 2.54 | 1.98 | 2.78 | 1.9841 | 2.54 |  | 11176 |  | 13020 | 1.62 |  | 1.9 | 2.02 |  | 2.00 | 59.18% | 76.14% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 8935198 | HRCU-A-CB | 4A6V0024A1 | *DHMB060BCV3 & 4PXCBD36BS3 | 24400 | 13 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22100 | 0.53 | 2.5 | 1.6 | 4.48 | 2.6018 | 4.04 |  | 11650 | 17400 | 17300 | 1.23 | 2.5 | 2.02 | 2.78 | 2.0393 | 2.5 |  | 11276 |  | 13220 | 1.64 |  | 1.92 | 2.02 |  | 2.00 | 59.82% | 76.42% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 8935199 | HRCU-A-CB | 4A6V0024A1 | *UD2B060ACV3 & 4TXCB004DS3 | 24200 | 13.5 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 7800 | 21200 | 21200 | 0.51 | 2.52 | 1.54 | 4.48 | 2.4649 | 4.04 |  | 11650 | 16800 | 16700 | 1.2 | 2.52 | 1.94 | 2.84 | 1.9533 | 2.52 |  | 11416 |  | 13200 | 1.6 |  | 1.86 | 2.10 |  | 2.10 | 62.26% | 79.04% | N/A |  |  | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8952869 | HRCU-A-CB-O | MOB30-09HFN1-MX0W | CS11M-09HRFN1-MX0W(A) | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2760 | 10900 | 15080 | 0.162 | 0.832 | 1.345 | 4.9931 | 3.8395 | 3.2859 |  | 2230 | 6900 | 11390 | 0.191 | 0.741 | 1.668 | 3.4217 | 2.729 | 2.0012 |  | 1931 |  | 10826 | 0.175 |  | 1.71 | 3.2338 |  | 1.8554 | 71.79% | 95.05% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8952870 | HRCU-A-CB-O | MOB30-12HFN1-MV0W | CS11M-12HRFN1-MU5W | 12000 | 13 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3658 | 11800 | 15135 | 0.188 | 0.994 | 1.35 | 5.7024 | 3.4791 | 3.2857 |  | 2931 | 7800 | 12448 | 0.226 | 0.866 | 1.96 | 3.8008 | 2.6397 | 1.8613 |  | 2558 |  | 12029 | 0.203 |  | 1.971 | 3.693 |  | 1.7886 | 79.48% | 96.63% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953943 | HMSV-A-CB | PUMY-P36NKMU1 | Non-ducted | 36000 | 14.2 | 21 | 11.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 13313 | 42000 | 42000 | 0.62 | 3.16 | 3.16 | 6.293 | 3.8952 | 3.8952 |  | 9690 | 26400 | 35000 | 0.726 | 2.59 | 3.799 | 3.9117 | 2.9873 | 2.7 |  | 6687 |  | 29000 | 0.582 |  | 3.695 | 3.3673 |  | 2.3002 | 69.05% | 80.17% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953944 | HMSV-A-CB | PUMY-P36NKMU1 | Ducted indoor units | 36000 | 12.6 | 15.6 | 10.5 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 13313 | 42000 | 42000 | 0.671 | 3.42 | 3.42 | 5.8147 | 3.5991 | 3.5991 |  | 9690 | 26600 | 36000 | 0.84 | 2.998 | 4.1 | 3.3809 | 2.6003 | 2.5733 |  | 6687 |  | 30000 | 0.63 |  | 3.9 | 3.1107 |  | 2.2544 | 71.43% | 75% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953946 | HMSV-A-CB | PUMY-P48NKMU1 | Non-ducted | 48000 | 12.6 | 20.2 | 11.7 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 15976 | 54000 | 54000 | 0.784 | 4.165 | 4.165 | 5.9721 | 3.7997 | 3.7997 |  | 11628 | 31400 | 43000 | 0.917 | 3.15 | 5.041 | 3.7163 | 2.9214 | 2.4999 |  | 8025 |  | 36400 | 0.735 |  | 4.849 | 3.1999 |  | 2.2 | 67.41% | 80.15% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953947 | HMSV-A-CB | PUMY-P60NKMU1 | Non-ducted | 60000 | 12.5 | 18.6 | 11.4 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 19526 | 66000 | 66000 | 1.027 | 5.53 | 5.53 | 5.5721 | 3.4978 | 3.4978 |  | 14121 | 41500 | 65000 | 1.201 | 4.68 | 8.283 | 3.446 | 2.5988 | 2.2998 |  | 9809 |  | 57000 | 0.963 |  | 8.353 | 2.9852 |  | 1.9999 | 86.36% | 80.18% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8989603 | HRCU-A-CB-O | MOBA30-09HFN1-MT0W | MSAEB-09HRFN1-MT0W | 9000 | 14 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3530 | 9800 | 13080 | 0.161 | 0.898 | 1.075 | 6.4257 | 3.1983 | 3.5659 |  | 2610 | 6300 | 8111 | 0.172 | 0.689 | 1.017 | 4.4472 | 2.6797 | 2.3374 |  | 2489 |  | 6609 | 0.159 |  | 1.01 | 4.5878 |  | 1.9177 | 50.53% | 81.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8993522 | HMSV-A-CB | MXZ-3C30NAHZ2 | Non-Ducted Indoor Units | 28400 | 12.5 | 18 | 11 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 |  | 25225 | 1.4 | 4.49 | 2.09 | 1.64
Lennox Industries, Inc. | Lennox | ML-Series | 8994418 | N/A | MLA030S4M-1P | Non-Ducted Indoor Units |  | 13 | 22 | 10.4 | Yes | Ductless | Multi-zone | N/A | 5820 | 28000 | 37720 | 0.895 | 2.345 | 3.475 | 1.9058 | 3.4994 | 3.1812 |  | 5411 | 18000 | 31054 | 0.924 | 1.925 | 4.176 | 1.7162 | 2.7404 | 2.1794 |  | 5145 |  | 28160 | 1.008 |  | 4.041 | 1.4959 |  | 2.0423 | 74.66% | 90.68% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Lennox Industries, Inc. | Lennox | ML-Series | 8994421 | N/A | MLA036S4M-1P | Non-Ducted Indoor Units |  | 13.5 | 21.5 | 10.5 | Yes | Ductless | Multi-zone | N/A | 7210 | 36000 | 50350 | 1.02 | 2.777 | 4.64 | 2.0716 | 3.7993 | 3.1802 |  | 6845 | 23200 | 38125 | 1.091 | 2.446 | 5.502 | 1.8387 | 2.7797 | 2.0308 |  | 6425 |  | 36000 | 1.146 |  | 5.379 | 1.6431 |  | 1.9614 | 71.5% | 94.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8996108 | HMSV-A-CB | MXZ-3C24NAHZ2 | Non-Ducted Indoor Units | 22000 | 13.5 | 19 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 |  | 22050 | 1.4 | 3.52 | 2.09 | 1.83
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Max Heat RAC Series | 9035283 | HRCU-A-CB-O | AR09KSWSPWKX | AR09KSWSPWKN | 9000 | 14.05 | 23.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 12000 | 12360 | 0.17 | 0.77 | 0.81 | 4.7064 | 4.5673 | 4.472 |  | 3105 | 6500 | 13990 | 0.27 | 0.8211 | 1.63 | 3.3703 | 2.32 | 2.5154 |  | 2730 |  | 12500 | 0.31 |  | 1.96 | 2.5809 |  | 1.8691 | 101.1% | 89.35% | Integrated | 230VAC 150W | Temp. below 0 degrees | -13°F | 2184 |  | 10000 | 0.26 | 1.67 | 2.4618 | 1.7549
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Max Heat RAC Series | 9035284 | HRCU-A-CB-O | AR12KSWSPWKX | AR12KSWSPWKN | 12000 | 12.5 | 21.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 14000 | 14420 | 0.17 | 0.97 | 1.0185 | 4.7064 | 4.2299 | 4.1493 |  | 3095 | 7500 | 16200 | 0.29 | 0.90454 | 1.9 | 3.1278 | 2.43 | 2.4988 |  | 2730 |  | 14200 | 0.33 |  | 2.25 | 2.4245 |  | 1.8496 | 98.47% | 87.65% | Integrated | 230VAC 150W | Temp. below 0 degrees | -13°F | 2184 |  | 11360 | 0.26 | 1.67 | 2.4618 | 1.9936
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038618 | HRCU-A-CB-O | WUHO09KW25S | WUHI09KHW | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038619 | HRCU-A-CB-O | WUHO12KW22S | WUHI12KHW | 12000 | 12.5 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.2998 | 3.5399 | 3.2699 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.6399 | 2.6399 | 2.2099 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038621 | HRCU-A-CB-O | WUHO24KW20S | WUHI24KHW | 24000 | 13 | 20.5 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.0298 | 3.5999 | 2.7199 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.7599 | 2.7599 | 1.9499 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.7799 |  | 1.8099 | 82.85% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038626 | HRCU-A-CB-O | WSM09MH20S/O | WSM09MH20S/I | 9000 | 14 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2908 | 9800 | 11602.2672 | 0.2454 | 0.89757 | 1.1766 | 3.4729 | 3.1999 | 2.8899 |  | 6300 | 6300 | 7979.9856 | 0.68896 | 0.68896 | 1.0929 | 2.6799 | 2.6799 | 2.1399 |  | 6600 |  | 6700 | 1.0075 |  | 1.0122 | 1.9199 |  | 1.9399 | 57.75% | 83.96% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038628 | HRCU-A-CB-O | WSM18MH20S/O | WSM18MH20S/I | 18000 | 13 | 22 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6093 | 18000 | 19146 | 0.37915 | 1.6695 | 1.5896 | 4.7097 | 3.1599 | 3.5299 |  | 11100 | 11100 | 12396 | 1.1787 | 1.1787 | 1.5013 | 2.7599 | 2.7599 | 2.4199 |  | 10460.09 |  | 12500 | 1.5252 |  | 2.0816 | 2.0099 |  | 1.7599 | 65.29% | 100.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038629 | HRCU-A-CB-O | WSM24MH20S/O | WSM24MH20S/I | 24000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 10271 | 25000 | 27303 | 0.64679 | 2.4588 | 3.5723 | 4.654 | 2.9799 | 2.2399 |  | 16000 | 16000 | 18330 | 1.9062 | 1.9062 | 2.798 | 2.4599 | 2.4599 | 1.9199 |  | 14800 |  | 15815 | 2.4786 |  | 2.6336 | 1.7499 |  | 1.7599 | 57.92% | 86.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084225 | HMSV-A-CB | GWHD(24)ND3GO | Non-Ducted Indoor Units | 24000 | 12.5 | 21 | 11 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7500 | 29000 | 35000 | 0.95 | 2.32 | 4.55 | 2.3137 | 3.6634 | 2.2544 |  | 17900 | 18800 | 23000 | 1.96 | 2 | 2.23 | 2.6765 | 2.7549 | 3.0227 |  | 17800 |  | 18356 | 2.79 |  | 2.97 | 1.8698 |  | 1.8113 | 52.45% | 79.81% | Integrated | 160 | When ambient temp ≤ 1 degree celsius | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084226 | HMSV-A-CB | GWHD(30)ND3GO | Non-Ducted Indoor Units | 28400 | 12.5 | 21 | 11.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8189 | 30000 | 32414 | 1.05 | 2.35 | 2.65 | 2.2857 | 3.7413 | 3.5848 |  | 17800 | 18100 | 24000 | 1.98 | 2.03 | 2.25 | 2.6347 | 2.6131 | 3.1261 |  | 18800 |  | 19356 | 2.89 |  | 3.01 | 1.9065 |  | 1.8846 | 59.71% | 80.65% | Integrated | 96 | When ambient temp ≤ 1 degree celsius | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084227 | HMSV-A-CB | GWHD(36)ND3GO | Non-Ducted Indoor Units | 34000 | 12.5 | 21 | 11.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8871 | 42500 | 44356 | 1.25 | 3.37 | 3.6 | 2.0799 | 3.696 | 3.611 |  | 19800 | 26500 | 27500 | 2.01 | 2.7 | 2.95 | 2.887 | 2.8764 | 2.732 |  | 20800 |  | 21356 | 2.99 |  | 3.12 | 2.0388 |  | 2.006 | 48.15% | 77.66% | Integrated | 96 | When ambient temp ≤ 1 degree celsius | N/A
Ouellet Canada Inc. | Ouellet | Champagne | 9085568 | HRCU-A-CB-O | OTP-C09000-E | OTP-C09000-I | 9000 | 14 | 23 | 10.5 | Yes | Ductless | Singlezone | Mini-Splits | 1911 | 11000 | 12000 | 0.16 | 1.02 | 1.35 | 3.5004 | 3.1606 | 2.6051 |  | 1750 | 6800 | 11546 | 0.13 | 0.98 | 1.548 | 3.9452 | 2.0336 | 2.1859 |  | 1450 |  | 9171 | 0.1 |  | 1.334 | 4.2495 |  | 2.0148 | 76.42% | 79.43% | Integrated | 68W | Heater on below 34°F | N/A | [7 empty] | 2018-03-05
Ouellet Canada Inc. | Ouellet | Champagne | 9085569 | HRCU-A-CB-O | OTP-C12000-E | OTP-C12000-I | 12000 | 12.5 | 22 | 11 | Yes | Ductless | Singlezone | Mini-Splits | 3100 | 13000 | 13000 | 0.2 | 0.96 | 1.35 | 4.5426 | 3.9687 | 2.8222 |  | 2610 | 7100 | 10918.4 | 0.19 | 0.84 | 1.35 | 4.0259 | 2.4771 | 2.3703 |  | 2376 |  | 8800 | 0.18 |  | 1.35 | 3.8685 |  | 1.9104 | 67.69% | 80.6% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 2018-03-05
Ouellet Canada Inc. | Ouellet | Champagne | 9085570 | HRCU-A-CB-O | OTP-C18000-E | OTP-C18000-I | 18000 | 12.5 | 20 | 10.5 | Yes | Ductless | Singlezone | Mini-Splits | 7340 | 19800 | 23500 | 0.58 | 1.73 | 2.6 | 3.7089 | 3.3542 | 2.6489 |  | 3900 | 12400 | 19000 | 0.29 | 1.35 | 2.6 | 3.9413 | 2.6919 | 2.1417 |  | 3600 |  | 16500 | 0.28 |  | 2.6 | 3.7681 |  | 1.8599 | 70.21% | 86.84% | Integrated | 160W | Under heating mode, the compressor in opening condition, while the outdoor ambient temperature is below 0 ℃, the pan heater begins to work. | N/A | [7 empty] | 2018-03-05
Ouellet Canada Inc. | Ouellet | Champagne | 9085571 | HRCU-A-CB-O | OTP-C24000-E | OTP-C24000-I | 22000 | 12.5 | 20 | 10 | Yes | Ductless | Singlezone | Mini-Splits | 6800 | 23000 | 30700 | 0.45 | 2 | 3 | 4.4286 | 3.3703 | 2.9991 |  | 4500 | 14600 | 24800 | 0.5 | 1.64 | 3.6 | 2.6376 | 2.609 | 2.0189 |  | 4000 |  | 20000 | 0.6 |  | 3.3 | 1.9538 |  | 1.7762 | 65.15% | 80.65% | Integrated | 160W | If T outer ring is less than T pan heater open temperature, then the pan heater works； | N/A | [7 empty] | 2018-03-05
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9104550 | HRCU-A-CB-O | MOD31-24HFN1-MT0W | MSAED-23HRFN1-MT0W | 24000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7200 | 25000 | 29140 | 0.36 | 2.459 | 2.603 | 5.8614 | 2.9796 | 3.2809 |  | 5690 | 16000 | 18650 | 0.486 | 1.906 | 2.478 | 3.4312 | 2.4602 | 2.2057 |  | 5122 |  | 15815 | 0.471 |  | 2.635 | 3.1871 |  | 1.759 | 54.27% | 84.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9104551 | HRCU-A-CB-O | MOCA31-18HFN1-MT0W | MSAED-18HRFN1-MT0W | 18000 | 13 | 22 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4670 | 18000 | 19190 | 0.231 | 1.669 | 1.674 | 5.9249 | 3.1607 | 3.3596 |  | 3920 | 11100 | 13730 | 0.262 | 1.179 | 1.615 | 4.3849 | 2.7592 | 2.4916 |  | 3274 |  | 12524 | 0.251 |  | 2.087 | 3.8228 |  | 1.7587 | 65.26% | 91.22% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9114294 | HRCU-A-CB-O | GWH18YE-D3DNA1A/O | GWH18AAE-D3DN***/I | 18000 | 13.5 | 24.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.5718 | 3.5169 | 2.309 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.4979 | 2.8297 | 2.1064 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.4192 |  | 2.0326 | 82.69% | 93.48% | N/A |  |  | N/A
Carrier | Carrier |  | 9118461 | HMSV-A-CB | 38MGRQ18B--3 | Non-Ducted Indoor Units | 18000 | 12.5 | 22.5 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 |  | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 |  | 4752 |  | 13990 | 0.58 |  | 1.91 | 2.4012 |  | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | Preferred Series | 9118462 | HMSV-A-CB | 38MGRQ18B--3 | Non-Ducted Indoor Units | 18000 | 12.5 | 22.5 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 |  | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 |  | 4752 |  | 13990 | 0.58 |  | 1.91 | 2.4012 |  | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier |  | 9118473 | HMSV-A-CB | 38MGRQ36D--3 | Non-Ducted Indoor Units | 36000 | 13.5 | 21.5 | 10.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 |  | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 |  | 7210 |  | 36080 | 1.2 |  | 5.39 | 1.7609 |  | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | Preferred Series | 9118474 | HMSV-A-CB | 38MGRQ36D--3 | Non-Ducted Indoor Units | 36000 | 13.5 | 21.5 | 10.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 |  | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 |  | 7210 |  | 36080 | 1.2 |  | 5.39 | 1.7609 |  | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier |  | 9118477 | HMSV-A-CB | 38MGRQ48E--3 | Non-Ducted Indoor Units | 48000 | 12.5 | 22.4 | 10.2 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 |  | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 |  | 6577 |  | 36340 | 1.1 |  | 5.39 | 1.7523 |  | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | Preferred Series | 9118478 | HMSV-A-CB | 38MGRQ48E--3 | Non-Ducted Indoor Units | 48000 | 12.5 | 22.4 | 10.2 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 |  | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 |  | 6577 |  | 36340 | 1.1 |  | 5.39 | 1.7523 |  | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | n/A |  | z
American Standard | American Standard | AccuComfort Platinum 18 | 9119381 | HRCU-A-CB | 4A6V8024A1 | *DHMB060BCV3 & 4PXCBD36BS3 | 24000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22100 | 0.53 | 2.5 | 1.6 | 4.48 | 2.6018 | 4.04 |  | 11650 | 17400 | 17300 | 1.23 | 2.5 | 2.02 | 2.78 | 2.0393 | 2.5 |  | 11276 |  | 13220 | 1.64 |  | 1.92 | 2.02 |  | 2.00 | 59.82% | 76.42% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 9122524 | HRCU-A-CB | 4A6V8024A1 | *DD2B060ACV3 & 4PXCBD36BS3 | 24000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22000 | 0.53 | 2.54 | 1.57 | 4.48 | 2.5608 | 4.1 |  | 11540 | 17200 | 17100 | 1.22 | 2.54 | 1.98 | 2.78 | 1.9841 | 2.54 |  | 11176 |  | 13020 | 1.62 |  | 1.9 | 2.02 |  | 2.00 | 59.18% | 76.14% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 9122736 | HRCU-A-CB | 4A6V0024A1 | *UHMB060ACV3 & 4PXCBU42BS3 | 24600 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 22200 | 22100 | 0.57 | 2.56 | 1.58 | 4.22 | 2.5408 | 4.1 |  | 12090 | 17300 | 17300 | 1.25 | 2.56 | 1.98 | 2.84 | 1.98 | 2.56 |  | 11782 |  | 13600 | 1.66 |  | 1.9 | 2.08 |  | 2.10 | 61.54% | 78.61% | N/A |  |  | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9123256 | HRCU-A-CB-O | GWH24YE-D3DNA1A/O | GWH24AAE-D3DN***/I | 22000 | 13 | 21.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5347 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6376 | 2.9376 | 2.2772 |  | 4000 |  | 22553 | 0.6 |  | 3.2 | 1.9538 |  | 2.0655 | 70.48% | 85.87% | N/A |  |  | N/A
Panasonic | Panasonic | Low-Profile Ducted | 9125308 | HRCU-A-CB-O | CU-E9SD3UA | CS-E9SD3UAW | 9000 | 13 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 9000 | 10200 | 0.25 | 0.69 | 0.85 | 4.8 | 3.82 | 3.53 |  | 3200 | 7900 | 9000 | 0.23 | 0.91 | 1.12 | 4.0801 | 2.5458 | 2.36 |  | 2400 |  | 7800 | 0.2 |  | 1.11 | 3.5191 |  | 2.0607 | 76.47% | 86.67% | N/A |  |  | -5°F | 1600 |  | 6700 | 0.16 | 1.1 | 2.9326 | 1.7862
Panasonic | Panasonic | Low-Profile Ducted | 9125309 | HRCU-A-CB-O | CU-E12SD3UA | CS-E12SD3UAW | 11500 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 11500 | 13300 | 0.25 | 0.92 | 1.15 | 4.8 | 3.64 | 3.39 |  | 3200 | 9500 | 11000 | 0.23 | 1.15 | 1.44 | 4.0801 | 2.4225 | 2.24 |  | 2400 |  | 9600 | 0.2 |  | 1.52 | 3.5191 |  | 1.8521 | 72.18% | 87.27% | N/A |  |  | -5°F | 1600 |  | 8200 | 0.16 | 1.6 | 2.9326 | 1.5029
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9141022 | HMSV-A-CB | PUMY-P36NKMU1 | Mixed | 36000 | 13.4 | 18.3 | 11 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 13313 | 42000 | 42000 | 0.646 | 3.29 | 3.29 | 6.0397 | 3.7413 | 3.7413 |  | 9690 | 26500 | 35500 | 0.783 | 2.794 | 3.95 | 3.627 | 2.7797 | 2.6339 |  | 6687 |  | 29000 | 0.606 |  | 3.798 | 3.2339 |  | 2.2378 | 69.05% | 77.39% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Trane | Trane |  | 9150121 | HRCU-A-CB-O | 4TXK3809A10NUAA | 4MXW3809A10NUAA | 9000 | 16.5 | 38 | 15 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12210 | 0.28 |  | 1.72 | 1.8265 |  | 2.0805 | 89.78% | 83.57% | Integrated | 72 | Heater on below 34°F | N/A
American Standard | American Standard |  | 9150122 | HRCU-A-CB-O | 4TXK3809A10NUAA | 4MXW3809A10NUAA | 9000 | 16.5 | 38 | 15 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12210 | 0.28 |  | 1.72 | 1.8265 |  | 2.0805 | 89.78% | 83.57% | Integrated | 72W | Heater on below 34°F | N/A
Trane | Trane |  | 9150123 | HRCU-A-CB-O | 4TXK3812A10NUAA | 4MXW3812A10NUAA | 12000 | 15.25 | 30.5 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 13304 | 0.22 |  | 1.789 | 3.4636 |  | 2.1794 | 71.14% | 147.8% | Integrated | 72 | Heater on below 34°F | N/A
American Standard | American Standard |  | 9150124 | HRCU-A-CB-O | 4TXK3812A10NUAA | 4MXW3812A10NUAA | 12000 | 15.25 | 30.5 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 13304 | 0.22 |  | 1.79 | 3.4636 |  | 2.1782 | 71.14% | 147.8% | Integrated | 72W | Heater on below 34°F | N/A
Trane | Trane |  | 9150125 | HRCU-A-CB-O | 4TXK3818A10NUAA | 4MXW3818A10NUAA | 18000 | 13.5 | 24.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 18000 | 24400 | 0.35 | 1.5 | 2.5 | 3.0982 | 3.5169 | 2.8604 |  | 3070 | 14200 | 23100 | 0.36 | 1.455 | 3.25 | 2.4992 | 2.8602 | 2.0831 |  | 2388 |  | 20634 | 0.37 |  | 3.3 | 1.8915 |  | 1.8325 | 84.57% | 89.32% | Integrated | 160 | Heater on below 34°F | N/A
American Standard | American Standard |  | 9150126 | HRCU-A-CB-O | 4TXK3818A10NUAA | 4MXW3818A10NUAA | 18000 | 13.5 | 24.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 18000 | 24400 | 0.35 | 1.5 | 2.5 | 3.0982 | 3.5169 | 2.8604 |  | 3070 | 14200 | 23100 | 0.36 | 1.455 | 3.25 | 2.4992 | 2.8602 | 2.0831 |  | 2388 |  | 20634 | 0.37 |  | 3.3 | 1.8915 |  | 1.8325 | 84.57% | 89.32% | Integrated | 160W | Heater on below 34°F | N/A
Trane | Trane |  | 9150127 | HRCU-A-CB-O | 4TXK3824A10NUAA | 4MXW3824A10NUAA | 22000 | 13 | 21.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32400 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5664 |  | 3396 | 15500 | 26263 | 0.344 | 1.57 | 3.381 | 2.8932 | 2.8934 | 2.2765 |  | 2887 |  | 24233 | 0.33 |  | 3.175 | 2.5639 |  | 2.2368 | 74.79% | 92.27% | Integrated | 160 | Heater on below 34°F | N/A
American Standard | American Standard |  | 9150128 | HRCU-A-CB-O | 4TXK3824A10NUAA | 4MXW3824A10NUAA | 22000 | 13 | 21.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32400 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5664 |  | 3396 | 15500 | 26263 | 0.344 | 1.57 | 3.381 | 2.8932 | 2.8934 | 2.2765 |  | 2887 |  | 24233 | 0.33 |  | 3.175 | 2.5639 |  | 2.2368 | 74.79% | 92.27% | Integrated | 160W | Heater on below 34°F | N/A
Panasonic | Panasonic | Wall Mounted | 9571162 | HRCU-A-CB-O | CU-XE15SKUA | CS-XE15SKUA | 15000 | 12.5 | 22.1 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3300 | 18000 | 24000 | 0.2 | 1.3 | 2.65 | 4.9 | 4.06 | 2.65 |  | 2000 | 11000 | 16500 | 0.16 | 1.02 | 2.3 | 3.6657 | 3.16 | 2.1 |  | 1500 |  | 15700 | 0.15 |  | 2.32 | 2.9326 |  | 1.98 | 65.42% | 95.15% | included with outdoor unit (Replacement part # CWA341072) | 100 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1100 |  | 14900 | 0.13 | 2.34 | 2.4814 | 1.8673
LG Electronics USA, Inc | LG |  | 9680934 | HRCU-A-CB-O | LAU180HYV2 | LAN180HYV2 | 18200 | 12.5 | 22 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 22000 | 32000 | 0.38 | 1.79 | 2.71 | 2.3677 | 3.602 | 3.4606 |  | 1810 | 13500 | 25640 | 0.36 | 1.44 | 2.84 | 1.4735 | 1.4736 | 2.6459 |  | 1350 |  | 22600 | 0.34 |  | 2.79 | 1.1637 |  | 2.374 | 70.62% | 88.14% | INTEGRATED | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
LG Electronics USA, Inc | LG |  | 9680935 | HRCU-A-CB-O | LAU150HYV2 | LAN150HYV2 | 15000 | 13.5 | 24 | 12.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 18000 | 25200 | 0.38 | 1.385 | 1.99 | 2.3677 | 3.8089 | 3.7113 |  | 1810 | 11000 | 20970 | 0.36 | 1.12 | 2.2 | 1.4735 | 1.4736 | 2.7935 |  | 1350 |  | 18940 | 0.34 |  | 2.16 | 1.1637 |  | 2.5698 | 75.16% | 90.32% | INTEGRATED | 120 | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680947 | HRCU-A-CB-O | MOBA30-09HFN1-MT0W | CS11M-09HRFN1-MX0W(A) | 9000 | 14.9 | 23.5 | 10.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 13360 | 0.144 | 0.756 | 1.1 | 6.124 | 3.7991 | 3.5595 |  | 2407 | 5800 | 8280 | 0.173 | 0.616 | 1.04 | 4.0776 | 2.7594 | 2.3333 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 59.81% | 96.5% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680948 | HRCU-A-CB-O | MOCA31-18HFN1-MT0W | CS11M-12HRFN1-MU5W | 12000 | 13.7 | 22.7 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 13660 | 0.177 | 0.999 | 1.1 | 6.4244 | 3.5204 | 3.6394 |  | 3104 | 7700 | 9930 | 0.212 | 0.816 | 1.35 | 4.291 | 2.7655 | 2.1557 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 66.87% | 91.98% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680949 | HRCU-A-CB-O | MOCA31-18HFN1-MT0W | CS11M-18HRFN1-MT0W | 18000 | 13 | 21 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 19590 | 0.231 | 1.589 | 1.71 | 6.1786 | 3.3199 | 3.3575 |  | 3896 | 11400 | 14020 | 0.277 | 1.228 | 1.65 | 4.122 | 2.7207 | 2.4902 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 57.06% | 79.73% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680950 | HRCU-A-CB-O | MOD31-24HFN1-MT0W | CS11M-23HRFN1-MT0W | 24000 | 13.7 | 20.7 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 29740 | 0.44 | 1.959 | 2.66 | 4.7291 | 3.7401 | 3.2767 |  | 5680 | 15300 | 19040 | 0.528 | 1.661 | 2.53 | 3.1527 | 2.6996 | 2.2056 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 60.86% | 95.06% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9722847 | HMSV-A-CB | MXZ-8C60NA | Non-ducted | 60000 | 12.5 | 17.4 | 10.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 19526 | 66000 | 66000 | 1.053 | 1.053 | 1.053 | 5.4345 | 3.4114 | 3.4114 |  | 14212 | 41500 | 65000 | 1.232 | 4.87 | 9.525 | 3.3809 | 2.4974 | 2 |  | 9808 |  | 57000 | 0.987 |  | 8.1 | 2.9123 |  | 2.0624 | 86.36% | 80.11% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Carrier | Carrier |  | 9854622 | HMSV-A-CB | 38MGRQ24C--3 | Non-Ducted Indoor Units | 24000 | 12.5 | 23 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 |  | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 |  | 5556 |  | 24170 | 0.84 |  | 3.9 | 1.9385 |  | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Carrier | Bryant | Preferred Series | 9854623 | HMSV-A-CB | 38MGRQ24C--3 | Non-Ducted Indoor Units | 24000 | 12.5 | 23 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 |  | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 |  | 5556 |  | 24170 | 0.84 |  | 3.9 | 1.9385 |  | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Carrier | Carrier |  | 9854626 | HMSV-A-CB | 38MGRQ30D--3 | Non-Ducted Indoor Units | 30000 | 12.5 | 23.8 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 |  | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0852 | 2.7866 | 2.1063 |  | 5164 |  | 28220 | 0.86 |  | 4.05 | 1.7598 |  | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant | Preferred Series | 9854627 | HMSV-A-CB | 38MGRQ30D--3 | Non-Ducted Indoor Units | 30000 | 12.5 | 23.8 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 |  | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 |  | 5164 |  | 28220 | 0.86 |  | 4.05 | 1.7598 |  | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Carrier | Carrier |  | 9892461 | HRCU-A-CB | 25VNA024A*030* | FE4ANB006L+UI | 25200 | 16 | 20.5 | 12 | Yes | Centrally Ducted | N/A | N/A | 14500 | 23600 | 23600 | 0.85 | 1.47 | 1.47 | 4.9994 | 4.7051 | 4.7051 |  | 13700 | 24800 | 24800 | 1.54 | 2.96 | 2.96 | 2.6072 | 2.4555 | 2.4555 |  | 10900 |  | 19600 | 1.47 |  | 2.77 | 2.1731 |  | 2.0737 | 83.05% | 79.03% | N/A |  |  | N/A
Carrier | Carrier |  | 9892512 | HRCU-A-CB | 25VNA024A*030* | FE4ANF002L + UI | 24200 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14800.2 | 24000 | 24000 | 0.8585 | 1.4847 | 1.4847 | 5.0524 | 4.7375 | 4.7375 |  | 14000 | 25200 | 25200 | 1.5554 | 2.8886 | 2.8886 | 2.6379 | 2.5567 | 2.5567 |  | 11100 |  | 19800 | 1.4847 |  | 2.7977 | 2.1911 |  | 2.0741 | 82.5% | 78.57% | N/A |  |  | N/A
Carrier | Carrier |  | 9892513 | HRCU-A-CB | 25VNA024A*030* | FE4AN(B,F)003L+UI | 24400 | 15 | 19.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14600 | 23800 | 23800 | 0.8585 | 1.4847 | 1.4847 | 4.9841 | 4.698 | 4.698 |  | 13850 | 25000 | 25000 | 1.5554 | 2.8886 | 2.8886 | 2.6096 | 2.5364 | 2.5364 |  | 11000 |  | 19800 | 1.4847 |  | 2.7977 | 2.1713 |  | 2.0741 | 83.19% | 79.2% | N/A |  |  | N/A
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892523 | HRCU-A-CB | 25VNA024A*030* | CAP**3617AL*+UI & 59*N*A060V17**14 | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6536 | 2.9631 | 2.9631 | 3.0562 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.4955 |  | 2.8766 | 2.3768 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892524 | HRCU-A-CB | 25VNA024A*030* | CAP**3617AL*+UI & 59*N*A080V17**14 | 24200 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7931 | 1.5096 | 1.5096 | 5.0117 | 4.6582 | 4.6582 |  | 17248.2 | 25200 | 25200 | 1.6377 | 2.9346 | 2.9346 | 3.0858 | 2.516 | 2.516 |  | 12131.88 |  | 21779.04 | 1.5102 |  | 2.849 | 2.3538 |  | 2.2398 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892525 | HRCU-A-CB | 25VNA024A*030* | CAP**3621AL*+UI & 59*N*A060V17**14 | 24200 | 14 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6536 | 2.9631 | 2.9631 | 3.0562 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892526 | HRCU-A-CB | 25VNA024A*030* | CAP**3621AL*+UI & 59*N*A080V17**14 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7931 | 1.5096 | 1.5096 | 5.0117 | 4.6582 | 4.6582 |  | 17248.2 | 25200 | 25200 | 1.6377 | 2.9346 | 2.9346 | 3.0858 | 2.516 | 2.516 |  | 12131.88 |  | 21779.04 | 1.5102 |  | 2.849 | 2.3538 |  | 2.2398 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892527 | HRCU-A-CB | 25VNA024A*030* | CAP**4221AL*+UI & 59*N*A060V17**14 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7777 | 1.4825 | 1.4825 | 5.0609 | 4.7039 | 4.7039 |  | 17079.1 | 25200 | 25200 | 1.6059 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 12012.94 |  | 21565.52 | 1.4809 |  | 2.7937 | 2.3768 |  | 2.2618 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892528 | HRCU-A-CB | 25VNA024A*030* | CAP**4221AL*+UI & 59*N*A080V17**14 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.77 | 1.4678 | 1.4678 | 5.1115 | 4.7509 | 4.7509 |  | 17079.1 | 25200 | 25200 | 1.59 | 2.8774 | 2.8774 | 3.1473 | 2.5661 | 2.5661 |  | 12012.94 |  | 21565.52 | 1.4662 |  | 2.766 | 2.4006 |  | 2.2844 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892529 | HRCU-A-CB | 25VNA024A*030* | CAP**4224AL*+UI & 59*N*A120V24**22 | 24400 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7623 | 1.4553 | 1.4553 | 5.112 | 4.7514 | 4.7514 |  | 16910 | 25000 | 25000 | 1.5741 | 2.8542 | 2.8542 | 3.1476 | 2.5663 | 2.5663 |  | 11894 |  | 21352 | 1.4515 |  | 2.7383 | 2.4008 |  | 2.2846 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892532 | HRCU-A-CB | 25VNA024A*030* | CAP**4821AL*+UI & 59*N*A060V17**14 | 24600 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.4787 | 2.736 | 2.736 | 3.2836 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892533 | HRCU-A-CB | 25VNA024A*030* | CAP**4821AL*+UI & 59*N*A080V17**14 | 24600 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 24800 | 24800 | 1.4787 | 2.7141 | 2.7141 | 3.2836 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 84.37% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892534 | HRCU-A-CB | 25VNA024A*030* | CAP**4824AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4628 | 2.7126 | 2.7126 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892535 | HRCU-A-CB | 25VNA024A*030* | CAP**6021AL*+UI & 59*N*A060V17**14 | 24600 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24600 | 24600 | 1.4469 | 2.6615 | 2.6615 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 84.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892536 | HRCU-A-CB | 25VNA024A*030* | CAP**6021AL*+UI & 59*N*A080V17**14 | 24600 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24600 | 24600 | 1.4469 | 2.6615 | 2.6615 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 84.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892537 | HRCU-A-CB | 25VNA024A*030* | CAP**6024AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12768 | 22600 | 22600 | 0.693 | 1.3197 | 1.3197 | 5.3983 | 5.0175 | 5.0175 |  | 16233.6 | 24400 | 24400 | 1.431 | 2.638 | 2.638 | 3.3238 | 2.7101 | 2.7101 |  | 11418.24 |  | 20497.92 | 1.3196 |  | 2.4894 | 2.5353 |  | 2.4126 | 90.7% | 84.01% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892538 | HRCU-A-CB | 25VNA024A*030* | CNPV*3617AL*+UI & 59*N*A060V17**14 | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8085 | 1.5389 | 1.5389 | 4.9163 | 4.5695 | 4.5695 |  | 17248.2 | 25400 | 25400 | 1.6695 | 3.0153 | 3.0153 | 3.0271 | 2.4681 | 2.4681 |  | 12131.88 |  | 21779.04 | 1.5395 |  | 2.9043 | 2.3089 |  | 2.1972 | 90.75% | 85.74% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892539 | HRCU-A-CB | 25VNA024A*030* | CNPV*3617AL*+UI & 59*N*A080V17**14 | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6536 | 2.9631 | 2.9631 | 3.0562 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892540 | HRCU-A-CB | 25VNA024A*030* | CNPV*3621AL*+UI & 59*N*A060V17**14 | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8085 | 1.5389 | 1.5389 | 4.9163 | 4.5695 | 4.5695 |  | 17248.2 | 25400 | 25400 | 1.6695 | 3.0153 | 3.0153 | 3.0271 | 2.4681 | 2.4681 |  | 12131.88 |  | 21779.04 | 1.5395 |  | 2.9043 | 2.3089 |  | 2.1972 | 90.75% | 85.74% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892541 | HRCU-A-CB | 25VNA024A*030* | CNPV*3621AL*+UI & 59*N*A080V17**14 | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6536 | 2.9631 | 2.9631 | 3.0562 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892542 | HRCU-A-CB | 25VNA024A*030* | CNPV*4217AL*+UI & 59*N*A060V17**14 | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7392 | 1.4134 | 1.4134 | 5.219 | 4.8509 | 4.8509 |  | 16740.9 | 25200 | 25200 | 1.5264 | 2.8181 | 2.8181 | 3.2135 | 2.6201 | 2.6201 |  | 11775.06 |  | 21138.48 | 1.4076 |  | 2.6554 | 2.4511 |  | 2.3325 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892543 | HRCU-A-CB | 25VNA024A*030* | CNPV*4217AL*+UI & 59*N*A080V17**14 | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7392 | 1.4134 | 1.4134 | 5.219 | 4.8509 | 4.8509 |  | 16740.9 | 25200 | 25200 | 1.5264 | 2.8181 | 2.8181 | 3.2135 | 2.6201 | 2.6201 |  | 11775.06 |  | 21138.48 | 1.4076 |  | 2.6554 | 2.4511 |  | 2.3325 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892544 | HRCU-A-CB | 25VNA024A*030* | CNPV*4221AL*+UI & 59*N*A060V17**14 | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.77 | 1.47 | 1.47 | 5.0609 | 4.7039 | 4.7039 |  | 16910 | 25200 | 25200 | 1.59 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11894 |  | 21352 | 1.4662 |  | 2.766 | 2.3768 |  | 2.2618 | 90.47% | 84.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892545 | HRCU-A-CB | 25VNA024A*030* | CNPV*4221AL*+UI & 59*N*A080V17**14 | 24200 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7623 | 1.4575 | 1.4575 | 5.0609 | 4.7039 | 4.7039 |  | 16740.9 | 25200 | 25200 | 1.5741 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11775.06 |  | 21138.48 | 1.4515 |  | 2.7383 | 2.3768 |  | 2.2618 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892546 | HRCU-A-CB | 25VNA024A*030* | CNPV*4821AL*+UI & 59*N*A060V17**14 | 24600 | 14.5 | 19.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7238 | 1.3839 | 1.3839 | 5.3301 | 4.9541 | 4.9541 |  | 16740.9 | 25000 | 25000 | 1.4946 | 2.7375 | 2.7375 | 3.2818 | 2.6758 | 2.6758 |  | 11775.06 |  | 21138.48 | 1.3782 |  | 2.6 | 2.5033 |  | 2.3821 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892547 | HRCU-A-CB | 25VNA024A*030* | CNPV*4821AL*+UI & 59*N*A080V17**14 | 24600 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.4787 | 2.736 | 2.736 | 3.2836 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892548 | HRCU-A-CB | 25VNA024A*030* | CNPV*4824AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.348 |  | 2.5447 | 2.5335 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892549 | HRCU-A-CB | 25VNA024A*030* | CNPV*6024AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.4787 | 2.7083 | 2.7083 | 3.3171 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892550 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59*N*A060V17**14 | 24400 | 14 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7623 | 1.4509 | 1.4509 | 5.2142 | 4.8464 | 4.8464 |  | 17248.2 | 25200 | 25200 | 1.5741 | 2.8207 | 2.8207 | 3.2105 | 2.6177 | 2.6177 |  | 12131.88 |  | 21779.04 | 1.4515 |  | 2.7383 | 2.4489 |  | 2.3303 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892551 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59*N*A080V17**14 | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7469 | 1.4237 | 1.4237 | 5.2696 | 4.8979 | 4.8979 |  | 17079.1 | 25200 | 25200 | 1.5423 | 2.791 | 2.791 | 3.2446 | 2.6454 | 2.6454 |  | 12012.94 |  | 21565.52 | 1.4222 |  | 2.683 | 2.4748 |  | 2.355 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892552 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59*N*A120V24**22 | 24600 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7469 | 1.4237 | 1.4237 | 5.2696 | 4.8979 | 4.8979 |  | 17079.1 | 25000 | 25000 | 1.5423 | 2.7689 | 2.7689 | 3.2446 | 2.6454 | 2.6454 |  | 12012.94 |  | 21565.52 | 1.4222 |  | 2.683 | 2.4748 |  | 2.355 | 90.61% | 86.26% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892553 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59*N*A060V17**14 | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7392 | 1.4091 | 1.4091 | 5.3245 | 4.9489 | 4.9489 |  | 17079.1 | 25200 | 25200 | 1.5264 | 2.7623 | 2.7623 | 3.2784 | 2.673 | 2.673 |  | 12012.94 |  | 21565.52 | 1.4076 |  | 2.6554 | 2.5006 |  | 2.3796 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892554 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59*N*A080V17**14 | 24800 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7392 | 1.4091 | 1.4091 | 5.3245 | 4.9489 | 4.9489 |  | 17079.1 | 25000 | 25000 | 1.5264 | 2.7403 | 2.7403 | 3.2784 | 2.673 | 2.673 |  | 12012.94 |  | 21565.52 | 1.4076 |  | 2.6554 | 2.5006 |  | 2.3796 | 90.61% | 86.26% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892555 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7315 | 1.3965 | 1.3965 | 5.3272 | 4.9515 | 4.9515 |  | 16910 | 25000 | 25000 | 1.5105 | 2.7389 | 2.7389 | 3.2801 | 2.6744 | 2.6744 |  | 11894 |  | 21352 | 1.3906 |  | 2.6277 | 2.506 |  | 2.3808 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892556 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59*N*A060V17**14 | 24800 | 14.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.4787 | 2.7083 | 2.7083 | 3.3171 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892557 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59*N*A080V17**14 | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.4787 | 2.7083 | 2.7083 | 3.3171 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892558 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59*N*A120V24**22 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4469 | 2.6771 | 2.6771 | 3.3558 | 2.7361 | 2.7361 |  | 11656.12 |  | 20924.96 | 1.3342 |  | 2.5171 | 2.5597 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892559 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59*N*A060V17**14 | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7238 | 1.3818 | 1.3818 | 5.3839 | 5.0042 | 5.0042 |  | 16910 | 25000 | 25000 | 1.4946 | 2.7101 | 2.7101 | 3.315 | 2.7028 | 2.7028 |  | 11894 |  | 21352 | 1.3782 |  | 2.6 | 2.5285 |  | 2.4061 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892560 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59*N*A080V17**14 | 25000 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7084 | 1.3545 | 1.3545 | 5.4459 | 5.0618 | 5.0618 |  | 16740.9 | 25000 | 25000 | 1.4628 | 2.6792 | 2.6792 | 3.3532 | 2.734 | 2.734 |  | 11775.06 |  | 21138.48 | 1.3489 |  | 2.5447 | 2.5577 |  | 2.4339 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892561 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59*N*A120V24**22 | 25000 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7084 | 1.3545 | 1.3545 | 5.4459 | 5.0618 | 5.0618 |  | 16740.9 | 25000 | 25000 | 1.4628 | 2.6792 | 2.6792 | 3.3532 | 2.734 | 2.734 |  | 11775.06 |  | 21138.48 | 1.3489 |  | 2.5447 | 2.5577 |  | 2.4339 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892562 | HRCU-A-CB | 25VNA024A*030* | CAP**3621AL*+UI & 59MN7A060V21**20 | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7777 | 1.4893 | 1.4893 | 4.9105 | 4.5642 | 4.5642 |  | 16571.8 | 25200 | 25200 | 1.6059 | 2.9951 | 2.9951 | 3.0235 | 2.4652 | 2.4652 |  | 11656.12 |  | 20924.96 | 1.4517 |  | 2.7937 | 2.3526 |  | 2.1946 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892563 | HRCU-A-CB | 25VNA024A*030* | CAP**3621AL*+UI & 59*N*A080V21**20 | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7623 | 1.4622 | 1.4622 | 4.9586 | 4.6089 | 4.6089 |  | 16402.7 | 25000 | 25000 | 1.5741 | 2.9425 | 2.9425 | 3.0531 | 2.4893 | 2.4893 |  | 11537.18 |  | 20711.44 | 1.4515 |  | 2.7383 | 2.3288 |  | 2.2161 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892564 | HRCU-A-CB | 25VNA024A*030* | CAP**3621AL*+UI & 59*N*A100V21**22 | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7546 | 1.4474 | 1.4474 | 5.0092 | 4.6559 | 4.6559 |  | 16402.7 | 25000 | 25000 | 1.5582 | 2.9128 | 2.9128 | 3.0843 | 2.5148 | 2.5148 |  | 11537.18 |  | 20711.44 | 1.4369 |  | 2.7107 | 2.3526 |  | 2.2387 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892565 | HRCU-A-CB | 25VNA024A*030* | CAP**4221AL*+UI & 59MN7A060V21**20 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7469 | 1.4326 | 1.4326 | 5.0609 | 4.7039 | 4.7039 |  | 16402.7 | 25200 | 25200 | 1.5423 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.683 | 2.4016 |  | 2.2618 | 90.05% | 82.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892566 | HRCU-A-CB | 25VNA024A*030* | CAP**4221AL*+UI & 59*N*A080V21**20 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.8533 | 2.8533 | 3.1486 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892567 | HRCU-A-CB | 25VNA024A*030* | CAP**4221AL*+UI & 59*N*A100V21**22 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.8533 | 2.8533 | 3.1486 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892568 | HRCU-A-CB | 25VNA024A*030* | CAP**4224AL*+UI & 59MN7A060V21**20 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7469 | 1.4326 | 1.4326 | 5.0609 | 4.7039 | 4.7039 |  | 16402.7 | 25200 | 25200 | 1.5423 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.683 | 2.4016 |  | 2.2618 | 90.05% | 82.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892569 | HRCU-A-CB | 25VNA024A*030* | CAP**4224AL*+UI & 59*N*A080V21**20 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.8533 | 2.8533 | 3.1486 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.3941 |  | 2.6554 | 2.4248 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892570 | HRCU-A-CB | 25VNA024A*030* | CAP**4224AL*+UI & 59*N*A100V21**22 | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.8533 | 2.8533 | 3.1486 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.3941 |  | 2.6554 | 2.4248 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892571 | HRCU-A-CB | 25VNA024A*030* | CAP**4821AL*+UI & 59MN7A060V21**20 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892572 | HRCU-A-CB | 25VNA024A*030* | CAP**4821AL*+UI & 59*N*A080V21**20 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892573 | HRCU-A-CB | 25VNA024A*030* | CAP**4821AL*+UI & 59*N*A100V21**22 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892574 | HRCU-A-CB | 25VNA024A*030* | CAP**4824AL*+UI & 59MN7A060V21**20 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3196 |  | 2.5171 | 2.5617 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892575 | HRCU-A-CB | 25VNA024A*030* | CAP**4824AL*+UI & 59*N*A080V21**20 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3227 |  | 2.5171 | 2.5557 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892576 | HRCU-A-CB | 25VNA024A*030* | CAP**4824AL*+UI & 59*N*A100V21**22 | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.693 | 1.3177 | 1.3177 | 5.4545 | 5.0698 | 5.0698 |  | 16402.7 | 24800 | 24800 | 1.431 | 2.6536 | 2.6536 | 3.3585 | 2.7383 | 2.7383 |  | 11537.18 |  | 20711.44 | 1.3227 |  | 2.4894 | 2.5557 |  | 2.4377 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892577 | HRCU-A-CB | 25VNA024A*030* | CAP**6021AL*+UI & 59MN7A060V21**20 | 24800 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4628 | 2.7126 | 2.7126 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5447 | 2.5335 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892578 | HRCU-A-CB | 25VNA024A*030* | CAP**6021AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892579 | HRCU-A-CB | 25VNA024A*030* | CAP**6021AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892580 | HRCU-A-CB | 25VNA024A*030* | CAP**6024AL*+UI & 59MN7A060V21**20 | 24800 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4628 | 2.7126 | 2.7126 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892581 | HRCU-A-CB | 25VNA024A*030* | CAP**6024AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892582 | HRCU-A-CB | 25VNA024A*030* | CAP**6024AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892583 | HRCU-A-CB | 25VNA024A*030* | CNPV*3621AL*+UI & 59MN7A060V21**20 | 24000 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7854 | 1.5017 | 1.5017 | 4.912 | 4.5656 | 4.5656 |  | 16740.9 | 25200 | 25200 | 1.6218 | 2.9942 | 2.9942 | 3.0244 | 2.466 | 2.466 |  | 11775.06 |  | 21138.48 | 1.4809 |  | 2.8213 | 2.3298 |  | 2.1953 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892584 | HRCU-A-CB | 25VNA024A*030* | CNPV*3621AL*+UI & 59*N*A080V21**20 | 24000 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7777 | 1.487 | 1.487 | 4.9606 | 4.6108 | 4.6108 |  | 16740.9 | 25200 | 25200 | 1.6059 | 2.9648 | 2.9648 | 3.0544 | 2.4904 | 2.4904 |  | 11775.06 |  | 21138.48 | 1.48 |  | 2.7937 | 2.3311 |  | 2.217 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892585 | HRCU-A-CB | 25VNA024A*030* | CNPV*3621AL*+UI & 59*N*A100V21**22 | 24000 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7777 | 1.487 | 1.487 | 4.9606 | 4.6108 | 4.6108 |  | 16740.9 | 25200 | 25200 | 1.6059 | 2.9648 | 2.9648 | 3.0544 | 2.4904 | 2.4904 |  | 11775.06 |  | 21138.48 | 1.4809 |  | 2.7937 | 2.3298 |  | 2.217 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892586 | HRCU-A-CB | 25VNA024A*030* | CNPV*4221AL*+UI & 59MN7A060V21**20 | 24400 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7623 | 1.4575 | 1.4575 | 5.0609 | 4.7039 | 4.7039 |  | 16740.9 | 25200 | 25200 | 1.5741 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11775.06 |  | 21138.48 | 1.4515 |  | 2.7383 | 2.3768 |  | 2.2618 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892587 | HRCU-A-CB | 25VNA024A*030* | CNPV*4221AL*+UI & 59*N*A080V21**20 | 24400 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7469 | 1.4303 | 1.4303 | 5.113 | 4.7524 | 4.7524 |  | 16571.8 | 25200 | 25200 | 1.5423 | 2.8765 | 2.8765 | 3.1482 | 2.5669 | 2.5669 |  | 11656.12 |  | 20924.96 | 1.4369 |  | 2.683 | 2.3768 |  | 2.2851 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892588 | HRCU-A-CB | 25VNA024A*030* | CNPV*4221AL*+UI & 59*N*A100V21**22 | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7469 | 1.4303 | 1.4303 | 5.113 | 4.7524 | 4.7524 |  | 16571.8 | 25000 | 25000 | 1.5423 | 2.8536 | 2.8536 | 3.1482 | 2.5669 | 2.5669 |  | 11656.12 |  | 20924.96 | 1.4369 |  | 2.683 | 2.3768 |  | 2.2851 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892589 | HRCU-A-CB | 25VNA024A*030* | CNPV*4824AL*+UI & 59MN7A060V21**20 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.4787 | 2.736 | 2.736 | 3.2836 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.348 |  | 2.5724 | 2.5335 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892590 | HRCU-A-CB | 25VNA024A*030* | CNPV*4824AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 25000 | 25000 | 1.4628 | 2.7345 | 2.7345 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3227 |  | 2.5447 | 2.5557 |  | 2.3847 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892591 | HRCU-A-CB | 25VNA024A*030* | CNPV*4824AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 25000 | 25000 | 1.4469 | 2.7047 | 2.7047 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892592 | HRCU-A-CB | 25VNA024A*030* | CNPV*6024AL*+UI & 59MN7A060V21**20 | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7238 | 1.3839 | 1.3839 | 5.3301 | 4.9541 | 4.9541 |  | 16740.9 | 25000 | 25000 | 1.4946 | 2.7375 | 2.7375 | 3.2818 | 2.6758 | 2.6758 |  | 11775.06 |  | 21138.48 | 1.3782 |  | 2.6 | 2.5033 |  | 2.3821 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892593 | HRCU-A-CB | 25VNA024A*030* | CNPV*6024AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3507 |  | 2.5447 | 2.5285 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892594 | HRCU-A-CB | 25VNA024A*030* | CNPV*6024AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3507 |  | 2.5447 | 2.5285 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892595 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59MN7A060V21**20 | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25200 | 25200 | 1.5105 | 2.8172 | 2.8172 | 3.2145 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.3929 |  | 2.6277 | 2.4519 |  | 2.3332 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892596 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59*N*A080V21**20 | 24600 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25000 | 25000 | 1.5105 | 2.7948 | 2.7948 | 3.2145 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.38 |  | 2.6277 | 2.4748 |  | 2.3332 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892597 | HRCU-A-CB | 25VNA024A*030* | CSPH*3612AL*+UI & 59*N*A100V21**22 | 24600 | 15 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25000 | 25000 | 1.5105 | 2.7948 | 2.7948 | 3.2145 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.38 |  | 2.6277 | 2.4748 |  | 2.3332 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892598 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59MN7A060V21**20 | 24800 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.4787 | 2.736 | 2.736 | 3.2836 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3628 |  | 2.5724 | 2.506 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892599 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892600 | HRCU-A-CB | 25VNA024A*030* | CSPH*4212AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 25000 | 25000 | 1.4628 | 2.7345 | 2.7345 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892601 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59MN7A060V21**20 | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.348 |  | 2.5447 | 2.5335 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892602 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59*N*A080V21**20 | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 25000 | 25000 | 1.4469 | 2.7047 | 2.7047 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.336 |  | 2.5171 | 2.5302 |  | 2.4109 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892603 | HRCU-A-CB | 25VNA024A*030* | CSPH*4812AL*+UI & 59*N*A100V21**22 | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.336 |  | 2.5171 | 2.5302 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892604 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59MN7A060V21**20 | 25000 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4469 | 2.6771 | 2.6771 | 3.3558 | 2.7361 | 2.7361 |  | 11656.12 |  | 20924.96 | 1.3342 |  | 2.5171 | 2.5597 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892605 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59*N*A080V21**20 | 25000 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4469 | 2603 | 2603 | 3.3558 | 2.74 | 2.74 |  | 11656.12 |  | 20924.96 | 1.3353 |  | 2.5171 | 2.5577 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892606 | HRCU-A-CB | 25VNA024A*030* | CSPH*6012AL*+UI & 59*N*A100V21**22 | 25000 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4469 | 2603 | 2603 | 3.3558 | 2.74 | 2.74 |  | 11656.12 |  | 20924.96 | 1.3353 |  | 2.5171 | 2.5577 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier |  | 9892607 | HRCU-A-CB | 25VNA036A*030* | FE4ANB006L+UI | 35000 | 14.5 | 20.5 | 13 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.07 | 2.07 | 4.1153 | 4.7288 | 4.7288 |  | 13250 | 31600 | 31600 | 1.83 | 3.3 | 3.3 | 2.122 | 2.8064 | 2.8064 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.6633 |  | 2.2027 | 70.66% | 74.68% | N/A |  |  | N/A
Carrier | Carrier |  | 9892658 | HRCU-A-CB | 25VNA036A*030* | FE4ANF002L+UI | 33000 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 |  | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.3838 |  | 11310.2 |  | 33496 | 2.1432 |  | 3.5796 | 1.5466 |  | 2.7424 | 94.62% | 109.5% | N/A |  |  | N/A
Carrier | Carrier |  | 9892659 | HRCU-A-CB | 25VNA036A*030* | FE4AN(B,F)003L+UI | 33400 | 13 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14273.8 | 35738 | 35600 | 1.083 | 2.3598 | 2.3598 | 3.8626 | 4.4384 | 4.4213 |  | 14177.5 | 33812 | 30200 | 2.0862 | 3.762 | 3.762 | 1.9917 | 2.6341 | 2.3527 |  | 11416.9 |  | 25252 | 2.1432 |  | 3.5796 | 1.5612 |  | 2.0674 | 70.93% | 83.62% | N/A |  |  | N/A
Carrier | Carrier |  | 9892665 | HRCU-A-CB | 25VNA036A*030* | FE4AN(B,F)005L+UI | 35000 | 13.5 | 20 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 1.0165 | 2.2149 | 2.2149 | 3.8461 | 4.4194 | 4.4194 |  | 13250 | 31600 | 31800 | 1.9581 | 3.531 | 3.531 | 1.9831 | 2.6228 | 2.6394 |  | 10670 |  | 23600 | 2.0116 |  | 3.3598 | 1.5545 |  | 2.0586 | 70.66% | 74.21% | N/A |  |  | N/A
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892672 | HRCU-A-CB | 25VNA036A*030* | CAP**4224AL*+UI & 59*N*A120V24**22 | 33600 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13965 | 35000 | 35000 | 0.8547 | 2.4593 | 2.4593 | 4.7873 | 4.1699 | 4.1699 |  | 17745 | 30200 | 30200 | 1.5651 | 3.6853 | 3.6853 | 3.322 | 2.401 | 2.401 |  | 12184.2 |  | 26961.9 | 2.0456 |  | 3.4282 | 1.7452 |  | 2.3044 | 77.03% | 89.28% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892676 | HRCU-A-CB | 25VNA036A*030* | CAP**4821AL*+UI & 59*N*A080V17**14 | 33600 | 12.5 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8393 | 2.4102 | 2.4102 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 32600 | 32600 | 1.5369 | 4.0612 | 4.0612 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0824 |  | 3.4898 | 1.6491 |  | 2.1774 | 77.19% | 79.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892677 | HRCU-A-CB | 25VNA036A*030* | CAP**4824AL*+UI & 59*N*A120V24**22 | 34200 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8085 | 2.3404 | 2.3404 | 4.7717 | 4.1563 | 4.1563 |  | 16731 | 32000 | 32000 | 1.4805 | 3.9177 | 3.9177 | 3.3111 | 2.3932 | 2.3932 |  | 11487.96 |  | 25421.22 | 1.8572 |  | 3.1126 | 1.8123 |  | 2.393 | 76.57% | 79.44% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892679 | HRCU-A-CB | 25VNA036A*030* | CAP**6021AL*+UI & 59*N*A080V17**14 | 34200 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33000 | 33000 | 0.8162 | 2.3485 | 2.3485 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 32000 | 32000 | 1.4946 | 3.955 | 3.955 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.1199 |  | 3.5527 | 1.5878 |  | 2.0965 | 77.03% | 79.44% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892680 | HRCU-A-CB | 25VNA036A*030* | CAP**6024AL*+UI & 59*N*A120V24**22 | 34400 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 32800 | 32800 | 0.8008 | 2.3136 | 2.3136 | 4.7689 | 4.1538 | 4.1538 |  | 16562 | 31600 | 31600 | 1.4664 | 3.871 | 3.871 | 3.3092 | 2.3918 | 2.3918 |  | 11371.92 |  | 25164.44 | 1.8197 |  | 3.0497 | 1.831 |  | 2.4177 | 76.72% | 79.63% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892690 | HRCU-A-CB | 25VNA036A*030* | CNPV*4821AL*+UI & 59*N*A080V17**14 | 34000 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.847 | 2.4515 | 2.4515 | 4.6928 | 4.0876 | 4.0876 |  | 17238 | 32600 | 32600 | 1.551 | 4.0583 | 4.0583 | 3.2564 | 2.3536 | 2.3536 |  | 11836.08 |  | 26191.56 | 2.0857 |  | 3.4955 | 1.6627 |  | 2.1954 | 76.58% | 80.34% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892691 | HRCU-A-CB | 25VNA036A*030* | CNPV*4824AL*+UI & 59*N*A120V24**22 | 34200 | 13.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 32200 | 32200 | 1.5087 | 3.8992 | 3.8992 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 1.8948 |  | 3.1754 | 1.8303 |  | 2.4167 | 77.03% | 81.34% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892692 | HRCU-A-CB | 25VNA036A*030* | CNPV*6024AL*+UI & 59*N*A120V24**22 | 35000 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8316 | 2.3881 | 2.3881 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32200 | 32200 | 1.5228 | 3.9746 | 3.9746 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 77.19% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892695 | HRCU-A-CB | 25VNA036A*030* | CSPH*3612AL*+UI & 59*N*A120V24**22 | 33600 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13965 | 35200 | 35200 | 0.8316 | 2.4065 | 2.4065 | 4.9203 | 4.2857 | 4.2857 |  | 17745 | 30400 | 30400 | 1.5228 | 3.6094 | 3.6094 | 3.4143 | 2.4677 | 2.4677 |  | 12184.2 |  | 26961.9 | 2.0618 |  | 3.4555 | 1.7314 |  | 2.2862 | 76.6% | 88.69% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892697 | HRCU-A-CB | 25VNA036A*030* | CSPH*4212AL*+UI & 59*N*A080V17**14 | 33600 | 12.5 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13832 | 34800 | 34800 | 0.8316 | 2.402 | 2.402 | 4.8734 | 4.2449 | 4.2449 |  | 17576 | 30600 | 30600 | 1.5228 | 3.6681 | 3.6681 | 3.3817 | 2.4442 | 2.4442 |  | 12068.16 |  | 26705.12 | 2.0625 |  | 3.4566 | 1.7144 |  | 2.2636 | 76.74% | 87.27% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892698 | HRCU-A-CB | 25VNA036A*030* | CSPH*4212AL*+UI & 59*N*A120V24**22 | 33800 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13832 | 34600 | 34600 | 0.8085 | 2.3219 | 2.3219 | 5.0127 | 4.3662 | 4.3662 |  | 17576 | 30200 | 30200 | 1.4805 | 3.5196 | 3.5196 | 3.4784 | 2.5141 | 2.5141 |  | 12068.16 |  | 26705.12 | 2.0261 |  | 3.3955 | 1.7452 |  | 2.3044 | 77.18% | 88.43% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892700 | HRCU-A-CB | 25VNA036A*030* | CSPH*4812AL*+UI & 59*N*A080V17**14 | 33600 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8316 | 2.4023 | 2.4023 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32800 | 32800 | 1.5228 | 4.0486 | 4.0486 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 2.0434 |  | 3.4245 | 1.6805 |  | 2.219 | 76.73% | 79.07% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892701 | HRCU-A-CB | 25VNA036A*030* | CSPH*4812AL*+UI & 59*N*A120V24**22 | 34000 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8085 | 2.3217 | 2.3217 | 4.8681 | 4.2402 | 4.2402 |  | 17069 | 32200 | 32200 | 1.4805 | 3.8642 | 3.8642 | 3.378 | 2.4415 | 2.4415 |  | 11720.04 |  | 25934.78 | 2.0261 |  | 3.3955 | 1.6949 |  | 2.2379 | 77.19% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892702 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59*N*A060V17**14 | 34200 | 12.5 | 18 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8162 | 2.3578 | 2.3578 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32600 | 32600 | 1.4946 | 3.9494 | 3.9494 | 3.3462 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.933 |  | 3.2396 | 1.7764 |  | 2.3456 | 76.73% | 79.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892703 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59*N*A080V17**14 | 34400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8162 | 2.3439 | 2.3439 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32400 | 32400 | 1.4946 | 3.9252 | 3.9252 | 3.3462 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.9886 |  | 3.3326 | 1.7268 |  | 2.2801 | 77.19% | 80.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892704 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59*N*A120V24**22 | 34600 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13300 | 33400 | 33400 | 0.7931 | 2.2866 | 2.2866 | 4.9135 | 4.2798 | 4.2798 |  | 16900 | 32000 | 32000 | 1.4523 | 3.8047 | 3.8047 | 3.4095 | 2.4643 | 2.4643 |  | 11604 |  | 25678 | 1.9689 |  | 3.2996 | 1.7268 |  | 2.2801 | 76.88% | 80.24% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892705 | HRCU-A-CB | 25VNA036A*030* | CAP**3621AL*+UI & 59MN7A060V21**20 | 33000 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8624 | 2.4814 | 2.4814 | 4.609 | 4.0146 | 4.0146 |  | 17238 | 30600 | 30600 | 1.5792 | 3.8786 | 3.8786 | 3.1983 | 2.3116 | 2.3116 |  | 11836.08 |  | 26191.56 | 2.1261 |  | 3.5632 | 1.6311 |  | 2.1537 | 77.03% | 85.59% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892706 | HRCU-A-CB | 25VNA036A*030* | CAP**3621AL*+UI & 59*N*A080V21**20 | 33400 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8547 | 2.4737 | 2.4737 | 4.6505 | 4.0507 | 4.0507 |  | 17238 | 30400 | 30400 | 1.5651 | 3.8188 | 3.8188 | 3.2271 | 2.3324 | 2.3324 |  | 11836.08 |  | 26191.56 | 2.1011 |  | 3.5213 | 1.6505 |  | 2.1793 | 76.58% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892707 | HRCU-A-CB | 25VNA036A*030* | CAP**3621AL*+UI & 59*N*A100V21**22 | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.847 | 2.4371 | 2.4371 | 4.6928 | 4.0876 | 4.0876 |  | 17238 | 30200 | 30200 | 1.551 | 3.7595 | 3.7595 | 3.2564 | 2.3536 | 2.3536 |  | 11836.08 |  | 26191.56 | 2.0824 |  | 3.4898 | 1.6654 |  | 2.199 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892708 | HRCU-A-CB | 25VNA036A*030* | CAP**4221AL*+UI & 59MN7A060V21**20 | 33200 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 30600 | 30600 | 1.5369 | 3.812 | 3.812 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0556 |  | 3.4451 | 1.6705 |  | 2.2057 | 76.73% | 84.75% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892709 | HRCU-A-CB | 25VNA036A*030* | CAP**4221AL*+UI & 59*N*A080V21**20 | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0651 |  | 3.4609 | 1.6793 |  | 2.2174 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892710 | HRCU-A-CB | 25VNA036A*030* | CAP**4221AL*+UI & 59*N*A100V21**22 | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892711 | HRCU-A-CB | 25VNA036A*030* | CAP**4224AL*+UI & 59MN7A060V21**20 | 33200 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 30400 | 30400 | 1.5369 | 3.7871 | 3.7871 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.003 |  | 3.3569 | 1.7144 |  | 2.2636 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892712 | HRCU-A-CB | 25VNA036A*030* | CAP**4224AL*+UI & 59*N*A080V21**20 | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0651 |  | 3.4609 | 1.6793 |  | 2.2174 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892713 | HRCU-A-CB | 25VNA036A*030* | CAP**4224AL*+UI & 59*N*A100V21**22 | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892714 | HRCU-A-CB | 25VNA036A*030* | CAP**4821AL*+UI & 59MN7A060V21**20 | 33800 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7931 | 2.2775 | 2.2775 | 4.9626 | 4.3226 | 4.3226 |  | 17069 | 30200 | 30200 | 1.4523 | 3.5551 | 3.5551 | 3.4436 | 2.489 | 2.489 |  | 11720.04 |  | 25934.78 | 2.0448 |  | 3.427 | 1.6793 |  | 2.2174 | 77.19% | 85.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892715 | HRCU-A-CB | 25VNA036A*030* | CAP**4821AL*+UI & 59*N*A080V21**20 | 34000 | 13 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7854 | 2.2554 | 2.2554 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.9323 |  | 3.2383 | 1.7771 |  | 2.3465 | 77.19% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892716 | HRCU-A-CB | 25VNA036A*030* | CAP**4821AL*+UI & 59*N*A100V21**22 | 34000 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892717 | HRCU-A-CB | 25VNA036A*030* | CAP**4824AL*+UI & 59MN7A060V21**20 | 34000 | 12.5 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 32800 | 32800 | 0.7777 | 2.2469 | 2.2469 | 4.9105 | 4.2772 | 4.2772 |  | 16562 | 30200 | 30200 | 1.4241 | 3.5928 | 3.5928 | 3.4075 | 2.4628 | 2.4628 |  | 11371.92 |  | 25164.44 | 1.9499 |  | 3.2679 | 1.7088 |  | 2.2563 | 76.72% | 83.33% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892718 | HRCU-A-CB | 25VNA036A*030* | CAP**4824AL*+UI & 59*N*A080V21**20 | 34000 | 13 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9528 |  | 3.2726 | 1.7585 |  | 2.3219 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892719 | HRCU-A-CB | 25VNA036A*030* | CAP**4824AL*+UI & 59*N*A100V21**22 | 34000 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892720 | HRCU-A-CB | 25VNA036A*030* | CAP**6021AL*+UI & 59MN7A060V21**20 | 34600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8316 | 2.4073 | 2.4073 | 4.6391 | 4.0408 | 4.0408 |  | 16731 | 32200 | 32200 | 1.5228 | 4.0549 | 4.0549 | 3.2192 | 2.3267 | 2.3267 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 78.95% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892721 | HRCU-A-CB | 25VNA036A*030* | CAP**6021AL*+UI & 59*N*A080V21**20 | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.0261 |  | 3.3955 | 1.6613 |  | 2.1936 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892722 | HRCU-A-CB | 25VNA036A*030* | CAP**6021AL*+UI & 59*N*A100V21**22 | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8008 | 2.3182 | 2.3182 | 4.8176 | 4.1962 | 4.1962 |  | 16731 | 31800 | 31800 | 1.4664 | 3.8562 | 3.8562 | 3.343 | 2.4162 | 2.4162 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892723 | HRCU-A-CB | 25VNA036A*030* | CAP**6024AL*+UI & 59MN7A060V21**20 | 34600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8316 | 2.4073 | 2.4073 | 4.6391 | 4.0408 | 4.0408 |  | 16731 | 32200 | 32200 | 1.5228 | 4.0549 | 4.0549 | 3.2192 | 2.3267 | 2.3267 |  | 11487.96 |  | 25421.22 | 1.9709 |  | 3.3031 | 1.7078 |  | 2.2549 | 76.57% | 78.95% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892724 | HRCU-A-CB | 25VNA036A*030* | CAP**6024AL*+UI & 59*N*A080V21**20 | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.0261 |  | 3.3955 | 1.6613 |  | 2.1936 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892725 | HRCU-A-CB | 25VNA036A*030* | CAP**6024AL*+UI & 59*N*A100V21**22 | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892727 | HRCU-A-CB | 25VNA036A*030* | CNPV*4221AL*+UI & 59*N*A080V21**20 | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8393 | 2.4292 | 2.4292 | 4.7359 | 4.1251 | 4.1251 |  | 17238 | 30400 | 30400 | 1.5369 | 3.75 | 3.75 | 3.2863 | 2.3752 | 2.3752 |  | 11836.08 |  | 26191.56 | 2.0681 |  | 3.466 | 1.6768 |  | 2.2141 | 76.58% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892728 | HRCU-A-CB | 25VNA036A*030* | CNPV*4221AL*+UI & 59*N*A100V21**22 | 33600 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8316 | 2.4069 | 2.4069 | 4.7797 | 4.1633 | 4.1633 |  | 17238 | 30200 | 30200 | 1.5228 | 3.6911 | 3.6911 | 3.3167 | 2.3972 | 2.3972 |  | 11836.08 |  | 26191.56 | 2.0448 |  | 3.427 | 1.6959 |  | 2.2393 | 76.58% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892729 | HRCU-A-CB | 25VNA036A*030* | CNPV*4821AL*+UI & 59MN7A060V21**20 | 33800 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 30400 | 30400 | 1.4664 | 3.6134 | 3.6134 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 2.0434 |  | 3.4245 | 1.6805 |  | 2.219 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892730 | HRCU-A-CB | 25VNA036A*030* | CNPV*4821AL*+UI & 59*N*A080V21**20 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7854 | 2.2688 | 2.2688 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.951 |  | 3.2698 | 1.7601 |  | 2.324 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892731 | HRCU-A-CB | 25VNA036A*030* | CNPV*4821AL*+UI & 59*N*A100V21**22 | 34200 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892732 | HRCU-A-CB | 25VNA036A*030* | CNPV*4824AL*+UI & 59MN7A060V21**20 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30400 | 30400 | 1.4805 | 3.6124 | 3.6124 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892733 | HRCU-A-CB | 25VNA036A*030* | CNPV*4824AL*+UI & 59*N*A080V21**20 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7854 | 2.2688 | 2.2688 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.9505 |  | 3.2688 | 1.7606 |  | 2.3246 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892734 | HRCU-A-CB | 25VNA036A*030* | CNPV*4824AL*+UI & 59*N*A100V21**22 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892735 | HRCU-A-CB | 25VNA036A*030* | CNPV*6024AL*+UI & 59MN7A060V21**20 | 34600 | 13 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8547 | 2.469 | 2.469 | 4.6049 | 4.011 | 4.011 |  | 17069 | 32400 | 32400 | 1.5651 | 4.1103 | 4.1103 | 3.1954 | 2.3096 | 2.3096 |  | 11720.04 |  | 25934.78 | 2.0261 |  | 3.3955 | 1.6949 |  | 2.2379 | 76.73% | 80.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892736 | HRCU-A-CB | 25VNA036A*030* | CNPV*6024AL*+UI & 59*N*A080V21**20 | 34800 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 32200 | 32200 | 1.5369 | 4.0114 | 4.0114 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0824 |  | 3.4898 | 1.6491 |  | 2.1774 | 76.73% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892737 | HRCU-A-CB | 25VNA036A*030* | CNPV*6024AL*+UI & 59*N*A100V21**22 | 34800 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8316 | 2.4023 | 2.4023 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32000 | 32000 | 1.5228 | 3.9499 | 3.9499 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 2.0448 |  | 3.427 | 1.6793 |  | 2.2174 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892739 | HRCU-A-CB | 25VNA036A*030* | CSPH*3612AL*+UI & 59*N*A080V21**20 | 33400 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30200 | 30200 | 1.4805 | 3.5886 | 3.5886 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892740 | HRCU-A-CB | 25VNA036A*030* | CSPH*3612AL*+UI & 59*N*A100V21**22 | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8008 | 2.3042 | 2.3042 | 4.9635 | 4.3234 | 4.3234 |  | 17238 | 30200 | 30200 | 1.4664 | 3.5544 | 3.5544 | 3.4443 | 2.4894 | 2.4894 |  | 11836.08 |  | 26191.56 | 1.9698 |  | 3.3012 | 1.7606 |  | 2.3246 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892741 | HRCU-A-CB | 25VNA036A*030* | CSPH*4212AL*+UI & 59MN7A060V21**20 | 33400 | 12.5 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30400 | 30400 | 1.4805 | 3.6124 | 3.6124 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 1.9319 |  | 3.2377 | 1.7951 |  | 2.3702 | 77.03% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892742 | HRCU-A-CB | 25VNA036A*030* | CSPH*4212AL*+UI & 59*N*A080V21**20 | 33400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.7854 | 2.2599 | 2.2599 | 5.0609 | 4.4082 | 4.4082 |  | 17238 | 30200 | 30200 | 1.4382 | 3.4861 | 3.4861 | 3.5118 | 2.5382 | 2.5382 |  | 11836.08 |  | 26191.56 | 1.9698 |  | 3.3012 | 1.7606 |  | 2.3246 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892743 | HRCU-A-CB | 25VNA036A*030* | CSPH*4212AL*+UI & 59*N*A100V21**22 | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892744 | HRCU-A-CB | 25VNA036A*030* | CSPH*4812AL*+UI & 59MN7A060V21**20 | 33800 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7931 | 2.2911 | 2.2911 | 4.9626 | 4.3226 | 4.3226 |  | 17069 | 30400 | 30400 | 1.4523 | 3.5787 | 3.5787 | 3.4436 | 2.489 | 2.489 |  | 11720.04 |  | 25934.78 | 1.9698 |  | 3.3012 | 1.7433 |  | 2.3018 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892745 | HRCU-A-CB | 25VNA036A*030* | CSPH*4812AL*+UI & 59*N*A080V21**20 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9323 |  | 3.2383 | 1.7771 |  | 2.3465 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892746 | HRCU-A-CB | 25VNA036A*030* | CSPH*4812AL*+UI & 59*N*A100V21**22 | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892747 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59MN7A060V21**20 | 34400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8162 | 2.3578 | 2.3578 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32200 | 32200 | 1.4946 | 3.901 | 3.901 | 3.3462 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.9516 |  | 3.2707 | 1.7595 |  | 2.3233 | 76.73% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892748 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59*N*A080V21**20 | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 32000 | 32000 | 1.4664 | 3.8036 | 3.8036 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 1.9886 |  | 3.3326 | 1.7268 |  | 2.2801 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892749 | HRCU-A-CB | 25VNA036A*030* | CSPH*6012AL*+UI & 59*N*A100V21**22 | 34800 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 32000 | 32000 | 1.4664 | 3.8036 | 3.8036 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 1.951 |  | 3.2698 | 1.7601 |  | 2.324 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier |  | 9892751 | HRCU-A-CB | 25VNA048A*030* | FE4ANB006L+UI | 47500 | 13.5 | 18 | 12 | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 2.96 | 2.96 | 4.4919 | 4.505 | 4.505 |  | 23840 | 47500 | 47500 | 2.66 | 5.66 | 5.66 | 2.6283 | 2.4595 | 2.4595 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.2101 | #DIV/0! | 2.2449 | 83.67% | 80.15% | N/A |  |  | N/A
Carrier | Carrier |  | 9892779 | HRCU-A-CB | 25VNA048A*030* | FE4AN(B,F)005L+UI | 46500 | 12.5 | 17.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 24800 | 46500 | 46500 | 1.7172 | 3.1968 | 3.1968 | 4.2326 | 4.263 | 4.263 |  | 24300 | 48500 | 48500 | 2.8728 | 6.1128 | 6.1128 | 2.479 | 2.3253 | 2.3253 |  | 19600 |  | 38800 | 2.754 |  | 5.3676 | 2.0858 |  | 2.1185 | 83.44% | 80% | N/A |  |  | N/A
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892783 | HRCU-A-CB | 25VNA048A*030* | CNPV*6024AL*+UI & 59*N*A120V24**22 | 46500 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25544 | 46000 | 46000 | 1.5606 | 3.2438 | 3.2438 | 4.7958 | 4.155 | 4.155 |  | 30179 | 49000 | 49000 | 2.8968 | 6.4052 | 6.4052 | 3.0525 | 2.2414 | 2.2414 |  | 21541.42 |  | 42258.84 | 2.4601 |  | 5.0735 | 2.5655 |  | 2.4405 | 91.87% | 86.24% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892794 | HRCU-A-CB | 25VNA048A*030* | CAP**6021AL*+UI & 59*N*A100V21**22 | 46000 | 12.5 | 17 | 11 | Yes | Centrally Ducted | N/A | N/A | 25048 | 45500 | 45500 | 1.5453 | 3.24 | 3.24 | 4.7492 | 4.1146 | 4.1146 |  | 29593 | 48000 | 48000 | 2.8684 | 6.336 | 6.336 | 3.0228 | 2.2197 | 2.2197 |  | 21123.14 |  | 41438.28 | 2.4566 |  | 5.0237 | 2.5193 |  | 2.4168 | 91.07% | 86.33% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892797 | HRCU-A-CB | 25VNA048A*030* | CAP**6024AL*+UI & 59*N*A100V21**22 | 46000 | 12.5 | 17 | 11 | Yes | Centrally Ducted | N/A | N/A | 24800 | 45500 | 45500 | 1.6065 | 3.402 | 3.402 | 4.5231 | 3.9187 | 3.9187 |  | 29300 | 48000 | 48000 | 2.982 | 6.6528 | 6.6528 | 2.8789 | 2.114 | 2.114 |  | 20914 |  | 41028 | 2.3885 |  | 5.2227 | 2.5655 |  | 2.3017 | 90.17% | 85.47% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892800 | HRCU-A-CB | 25VNA048A*030* | CNPV*4821AL*+UI & 59*N*A100V21**22 | 45500 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 26040 | 46000 | 46000 | 1.5912 | 3.2444 | 3.2444 | 4.7949 | 4.1542 | 4.1542 |  | 30765 | 48000 | 48000 | 2.9536 | 6.2757 | 6.2757 | 3.0519 | 2.241 | 2.241 |  | 21959.7 |  | 43079.4 | 2.5311 |  | 5.173 | 2.542 |  | 2.44 | 93.65% | 89.75% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892805 | HRCU-A-CB | 25VNA048A*030* | CNPV*6024AL*+UI & 59*N*A080V21**20 | 46000 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25072.8 | 46000 | 46000 | 1.6677 | 3.5316 | 3.5316 | 4.405 | 3.8164 | 3.8164 |  | 29622.3 | 49000 | 49000 | 3.0956 | 6.9734 | 6.9734 | 2.8037 | 2.0588 | 2.0588 |  | 21144.054 |  | 41479.308 | 2.4148 |  | 5.4217 | 2.5655 |  | 2.2416 | 90.17% | 84.65% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier® Air Conditioning | Infinity® 20 Heat Pump with Greenspeed® Intelligence | 9892806 | HRCU-A-CB | 25VNA048A*030* | CNPV*6024AL*+UI & 59*N*A100V21**22 | 46000 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25072.8 | 46000 | 46000 | 1.6509 | 3.4959 | 3.4959 | 4.4499 | 3.8553 | 3.8553 |  | 29622.3 | 48500 | 48500 | 3.0644 | 6.8326 | 6.8326 | 2.8323 | 2.0798 | 2.0798 |  | 21144.054 |  | 41479.308 | 2.4148 |  | 5.3669 | 2.5655 |  | 2.2645 | 90.17% | 85.52% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Carrier | Carrier |  | 9892813 | HRCU-A-CB | 25VNA060A*030* | FE4ANB006L+UI | 56000 | 12.5 | 18 | 12 | Yes | Centrally Ducted | N/A | N/A | 24600 | 55500 | 55500 | 1.75 | 4.15 | 4.15 | 4.1197 | 3.9194 | 3.9194 |  | 24160 | 52500 | 52500 | 2.93 | 6.91 | 6.91 | 2.4166 | 2.2267 | 2.2267 |  | 19400 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893411 | HRCU-A-CB | 280ANV024000 | FE4ANB006L+UI | 25200 | 16 | 20.5 | 12 | Yes | Centrally Ducted | N/A | N/A | 14500 | 23600 | 23600 | 0.85 | 1.47 | 1.47 | 4.9994 | 4.7051 | 4.7051 |  | 13700 | 24800 | 24800 | 1.54 | 2.96 | 2.96 | 2.6072 | 2.4555 | 2.4555 |  | 10900 |  | 19600 | 1.47 |  | 2.77 | 2.1731 |  | 2.0737 | 83.05% | 79.03% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893462 | HRCU-A-CB | 280ANV024000 | FE4ANF002L+UI | 24200 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14800.2 | 24000 | 24000 | 0.8585 | 1.4847 | 1.4847 | 5.0524 | 4.7375 | 4.7375 |  | 14000 | 25200 | 25200 | 1.5554 | 2.8886 | 2.8886 | 2.6379 | 2.5567 | 2.5567 |  | 11100 |  | 19800 | 1.4847 |  | 2.7977 | 2.1911 |  | 2.0741 | 82.5% | 78.57% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893463 | HRCU-A-CB | 280ANV024000 | FE4AN(B,F)003+UI | 24400 | 15 | 19.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14600 | 23800 | 23800 | 0.8585 | 1.4847 | 1.4847 | 4.9841 | 4.698 | 4.698 |  | 13850 | 25000 | 25000 | 1.5554 | 2.8886 | 2.8886 | 2.6096 | 2.5364 | 2.5364 |  | 11000 |  | 19800 | 1.4847 |  | 2.7977 | 2.1713 |  | 2.0741 | 83.19% | 79.2% | N/A |  |  | N/A
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893473 | HRCU-A-CB | 280ANV024*0**A* | CAP**3617AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6536 | 2.9631 | 2.9631 | 3.0562 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893474 | HRCU-A-CB | 280ANV024*0**A* | CAP**3617AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7931 | 1.5096 | 1.5096 | 5.0117 | 4.6582 | 4.6582 |  | 17248.2 | 25200 | 25200 | 1.5727 | 2.9346 | 2.9346 | 3.2135 | 2.516 | 2.516 |  | 12131.88 |  | 21779.04 | 1.5102 |  | 2.849 | 2.3538 |  | 2.2398 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893475 | HRCU-A-CB | 280ANV024*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.6695 | 2.9631 | 2.9631 | 3.0271 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893476 | HRCU-A-CB | 280ANV024*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7931 | 1.5096 | 1.5096 | 5.0117 | 4.6582 | 4.6582 |  | 17248.2 | 25200 | 25200 | 1.5391 | 2.9346 | 2.9346 | 3.2836 | 2.516 | 2.516 |  | 12131.88 |  | 21779.04 | 1.5102 |  | 2.849 | 2.3538 |  | 2.2398 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893477 | HRCU-A-CB | 280ANV024*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7777 | 1.4825 | 1.4825 | 5.0609 | 4.7039 | 4.7039 |  | 17079.1 | 25200 | 25200 | 1.6531 | 2.9061 | 2.9061 | 3.0271 | 2.5407 | 2.5407 |  | 12012.94 |  | 21565.52 | 1.4809 |  | 2.7937 | 2.3768 |  | 2.2618 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893478 | HRCU-A-CB | 280ANV024*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.77 | 1.4678 | 1.4678 | 5.1115 | 4.7509 | 4.7509 |  | 17079.1 | 25200 | 25200 | 1.5423 | 2.8774 | 2.8774 | 3.2446 | 2.5661 | 2.5661 |  | 12012.94 |  | 21565.52 | 1.4662 |  | 2.766 | 2.4006 |  | 2.2844 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893479 | HRCU-A-CB | 280ANV024*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)66120V24*** | 24400 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7623 | 1.4553 | 1.4553 | 5.112 | 4.7514 | 4.7514 |  | 16910 | 25000 | 25000 | 1.508 | 2.8542 | 2.8542 | 3.2854 | 2.5663 | 2.5663 |  | 11894 |  | 21352 | 1.4515 |  | 2.7383 | 2.4008 |  | 2.2846 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893482 | HRCU-A-CB | 280ANV024*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)42060V17*** | 24600 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.4647 | 2.736 | 2.736 | 3.315 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893483 | HRCU-A-CB | 280ANV024*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)42080V17*** | 24600 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 24800 | 24800 | 1.5888 | 2.7141 | 2.7141 | 3.0562 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 84.37% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893484 | HRCU-A-CB | 280ANV024*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.7126 | 2.7126 | 3.3215 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893485 | HRCU-A-CB | 280ANV024*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)42060V17*** | 24600 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24600 | 24600 | 1.4644 | 2.6615 | 2.6615 | 3.2818 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 84.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893486 | HRCU-A-CB | 280ANV024*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)42080V17*** | 24600 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24600 | 24600 | 1.5423 | 2.6615 | 2.6615 | 3.1161 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 84.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893487 | HRCU-A-CB | 280ANV024*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12768 | 22600 | 22600 | 0.693 | 1.3197 | 1.3197 | 5.3983 | 5.0175 | 5.0175 |  | 16233.6 | 24400 | 24400 | 1.4329 | 2.638 | 2.638 | 3.3193 | 2.7101 | 2.7101 |  | 11418.24 |  | 20497.92 | 1.3196 |  | 2.4894 | 2.5353 |  | 2.4126 | 90.7% | 84.01% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893488 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3617AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8085 | 1.5389 | 1.5389 | 4.9163 | 4.5695 | 4.5695 |  | 17248.2 | 25400 | 25400 | 1.6536 | 3.0153 | 3.0153 | 3.0562 | 2.4681 | 2.4681 |  | 12131.88 |  | 21779.04 | 1.5395 |  | 2.9043 | 2.3089 |  | 2.1972 | 90.75% | 85.74% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893489 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3617AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.5215 | 2.9631 | 2.9631 | 3.3215 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893490 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3621AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14 | 18.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8085 | 1.5389 | 1.5389 | 4.9163 | 4.5695 | 4.5695 |  | 17248.2 | 25400 | 25400 | 1.5741 | 3.0153 | 3.0153 | 3.2105 | 2.4681 | 2.4681 |  | 12131.88 |  | 21779.04 | 1.5395 |  | 2.9043 | 2.3089 |  | 2.1972 | 90.75% | 85.74% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893491 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3621AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.8008 | 1.5242 | 1.5242 | 4.9635 | 4.6134 | 4.6134 |  | 17248.2 | 25200 | 25200 | 1.5391 | 2.9631 | 2.9631 | 3.2836 | 2.4918 | 2.4918 |  | 12131.88 |  | 21779.04 | 1.5248 |  | 2.8766 | 2.3311 |  | 2.2183 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893492 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4217AL*+UI & 98(6*B,7*A)42060V17*** | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7392 | 1.4134 | 1.4134 | 5.219 | 4.8509 | 4.8509 |  | 16740.9 | 25200 | 25200 | 1.4787 | 2.8181 | 2.8181 | 3.3171 | 2.6201 | 2.6201 |  | 11775.06 |  | 21138.48 | 1.4076 |  | 2.6554 | 2.4511 |  | 2.3325 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893493 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4217AL*+UI & 98(6*B,7*A)42080V17*** | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7392 | 1.4134 | 1.4134 | 5.219 | 4.8509 | 4.8509 |  | 16740.9 | 25200 | 25200 | 1.5585 | 2.8181 | 2.8181 | 3.1473 | 2.6201 | 2.6201 |  | 11775.06 |  | 21138.48 | 1.4076 |  | 2.6554 | 2.4511 |  | 2.3325 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893494 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)42060V17*** | 24200 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.77 | 1.47 | 1.47 | 5.0609 | 4.7039 | 4.7039 |  | 16910 | 25200 | 25200 | 1.59 | 2.9061 | 2.9061 | 3.1161 | 2.5407 | 2.5407 |  | 11894 |  | 21352 | 1.4662 |  | 2.766 | 2.3768 |  | 2.2618 | 90.47% | 84.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893495 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)42080V17*** | 24200 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7623 | 1.4575 | 1.4575 | 5.0609 | 4.7039 | 4.7039 |  | 16740.9 | 25200 | 25200 | 1.5895 | 2.9061 | 2.9061 | 3.0858 | 2.5407 | 2.5407 |  | 11775.06 |  | 21138.48 | 1.4515 |  | 2.7383 | 2.3768 |  | 2.2618 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893496 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)42060V17*** | 24600 | 14.5 | 19.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7238 | 1.3839 | 1.3839 | 5.3301 | 4.9541 | 4.9541 |  | 16740.9 | 25000 | 25000 | 1.4962 | 2.7375 | 2.7375 | 3.2784 | 2.6758 | 2.6758 |  | 11775.06 |  | 21138.48 | 1.3782 |  | 2.6 | 2.5033 |  | 2.3821 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893497 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)42080V17*** | 24600 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.448 | 2.736 | 2.736 | 3.3532 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893498 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4638 | 2.7066 | 2.7066 | 3.3171 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893499 | HRCU-A-CB | 280ANV024*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.4617 | 2.7083 | 2.7083 | 3.3558 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893500 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)42060V17*** | 24400 | 14 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 24000 | 24000 | 0.7623 | 1.4509 | 1.4509 | 5.2142 | 4.8464 | 4.8464 |  | 17248.2 | 25200 | 25200 | 1.5727 | 2.8207 | 2.8207 | 3.2135 | 2.6177 | 2.6177 |  | 12131.88 |  | 21779.04 | 1.4515 |  | 2.7383 | 2.4489 |  | 2.3303 | 90.75% | 86.42% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893501 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)42080V17*** | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7469 | 1.4237 | 1.4237 | 5.2696 | 4.8979 | 4.8979 |  | 17079.1 | 25200 | 25200 | 1.6374 | 2.791 | 2.791 | 3.0562 | 2.6454 | 2.6454 |  | 12012.94 |  | 21565.52 | 1.4222 |  | 2.683 | 2.4748 |  | 2.355 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893502 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)66120V24*** | 24600 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7469 | 1.4237 | 1.4237 | 5.2696 | 4.8979 | 4.8979 |  | 17079.1 | 25000 | 25000 | 1.4924 | 2.7689 | 2.7689 | 3.3532 | 2.6454 | 2.6454 |  | 12012.94 |  | 21565.52 | 1.4222 |  | 2.683 | 2.4748 |  | 2.355 | 90.61% | 86.26% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893503 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)42060V17*** | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7392 | 1.4091 | 1.4091 | 5.3245 | 4.9489 | 4.9489 |  | 17079.1 | 25200 | 25200 | 1.524 | 2.7623 | 2.7623 | 3.2836 | 2.673 | 2.673 |  | 12012.94 |  | 21565.52 | 1.4076 |  | 2.6554 | 2.5006 |  | 2.3796 | 90.61% | 85.58% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893504 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)42080V17*** | 24800 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 23800 | 23800 | 0.7392 | 1.4091 | 1.4091 | 5.3245 | 4.9489 | 4.9489 |  | 17079.1 | 25000 | 25000 | 1.5086 | 2.7403 | 2.7403 | 3.3171 | 2.673 | 2.673 |  | 12012.94 |  | 21565.52 | 1.4076 |  | 2.6554 | 2.5006 |  | 2.3796 | 90.61% | 86.26% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893505 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7315 | 1.3965 | 1.3965 | 5.3272 | 4.9515 | 4.9515 |  | 16910 | 25000 | 25000 | 1.4906 | 2.7389 | 2.7389 | 3.3238 | 2.6744 | 2.6744 |  | 11894 |  | 21352 | 1.3929 |  | 2.6277 | 2.5019 |  | 2.3808 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893506 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)42060V17*** | 24800 | 14.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.4767 | 2.7083 | 2.7083 | 3.3215 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893507 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)42080V17*** | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7161 | 1.3692 | 1.3692 | 5.3874 | 5.0074 | 5.0074 |  | 16740.9 | 25000 | 25000 | 1.5741 | 2.7083 | 2.7083 | 3.1161 | 2.7046 | 2.7046 |  | 11775.06 |  | 21138.48 | 1.3636 |  | 2.5724 | 2.5302 |  | 2.4077 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893508 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)66120V24*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.5426 | 2.6771 | 2.6771 | 3.1476 | 2.7361 | 2.7361 |  | 11656.12 |  | 20924.96 | 1.3342 |  | 2.5171 | 2.5597 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893509 | HRCU-A-CB | 280ANV024*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)42060V17*** | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13300 | 23600 | 23600 | 0.7238 | 1.3818 | 1.3818 | 5.3839 | 5.0042 | 5.0042 |  | 16910 | 25000 | 25000 | 1.6212 | 2.7101 | 2.7101 | 3.0562 | 2.7028 | 2.7028 |  | 11894 |  | 21352 | 1.3782 |  | 2.6 | 2.5285 |  | 2.4061 | 90.47% | 85.41% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893510 | HRCU-A-CB | 280ANV024*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)42080V17*** | 25000 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7084 | 1.3545 | 1.3545 | 5.4459 | 5.0618 | 5.0618 |  | 16740.9 | 25000 | 25000 | 1.4962 | 2.6792 | 2.6792 | 3.2784 | 2.734 | 2.734 |  | 11775.06 |  | 21138.48 | 1.3489 |  | 2.5447 | 2.5577 |  | 2.4339 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893511 | HRCU-A-CB | 280ANV024*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)66120V24*** | 25000 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7084 | 1.3545 | 1.3545 | 5.4459 | 5.0618 | 5.0618 |  | 16740.9 | 25000 | 25000 | 1.4954 | 2.6792 | 2.6792 | 3.2801 | 2.734 | 2.734 |  | 11775.06 |  | 21138.48 | 1.3489 |  | 2.5447 | 2.5577 |  | 2.4339 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893512 | HRCU-A-CB | 280ANV024*0**A* | CAP**3621AL*+UI & 98(6*B,7MA)60060V21*** | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7777 | 1.4893 | 1.4893 | 4.9105 | 4.5642 | 4.5642 |  | 16571.8 | 25200 | 25200 | 1.5582 | 2.9951 | 2.9951 | 3.1161 | 2.4652 | 2.4652 |  | 11656.12 |  | 20924.96 | 1.4809 |  | 2.7937 | 2.3062 |  | 2.1946 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893513 | HRCU-A-CB | 280ANV024*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)60080V21*** | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7623 | 1.4622 | 1.4622 | 4.9586 | 4.6089 | 4.6089 |  | 16402.7 | 25000 | 25000 | 1.4479 | 2.9425 | 2.9425 | 3.3193 | 2.4893 | 2.4893 |  | 11537.18 |  | 20711.44 | 1.4515 |  | 2.7383 | 2.3288 |  | 2.2161 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893514 | HRCU-A-CB | 280ANV024*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)66100V21*** | 24000 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7546 | 1.4474 | 1.4474 | 5.0092 | 4.6559 | 4.6559 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.9128 | 2.9128 | 3.1486 | 2.5148 | 2.5148 |  | 11537.18 |  | 20711.44 | 1.4369 |  | 2.7107 | 2.3526 |  | 2.2387 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893515 | HRCU-A-CB | 280ANV024*0**A* | CAP**4221AL*+UI & 98(6*B,7MA)60060V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7469 | 1.4326 | 1.4326 | 5.0609 | 4.7039 | 4.7039 |  | 16402.7 | 25200 | 25200 | 1.5895 | 2.9061 | 2.9061 | 3.0235 | 2.5407 | 2.5407 |  | 11537.18 |  | 20711.44 | 1.4222 |  | 2.683 | 2.3768 |  | 2.2618 | 90.05% | 82.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893516 | HRCU-A-CB | 280ANV024*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)60080V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.4469 | 2.8533 | 2.8533 | 3.3215 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893517 | HRCU-A-CB | 280ANV024*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)66100V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.4469 | 2.8533 | 2.8533 | 3.3215 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893518 | HRCU-A-CB | 280ANV024*0**A* | CAP**4224AL*+UI & 98(6*B,7MA)60060V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7469 | 1.4326 | 1.4326 | 5.0609 | 4.7039 | 4.7039 |  | 16402.7 | 25200 | 25200 | 1.4479 | 2.9061 | 2.9061 | 3.3193 | 2.5407 | 2.5407 |  | 11537.18 |  | 20711.44 | 1.4222 |  | 2.683 | 2.3768 |  | 2.2618 | 90.05% | 82.19% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893519 | HRCU-A-CB | 280ANV024*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)60080V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5735 | 2.8533 | 2.8533 | 3.0544 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893520 | HRCU-A-CB | 280ANV024*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)66100V21*** | 24200 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7392 | 1.4179 | 1.4179 | 5.1136 | 4.7529 | 4.7529 |  | 16402.7 | 25000 | 25000 | 1.5266 | 2.8533 | 2.8533 | 3.1482 | 2.5671 | 2.5671 |  | 11537.18 |  | 20711.44 | 1.4076 |  | 2.6554 | 2.4016 |  | 2.2853 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893521 | HRCU-A-CB | 280ANV024*0**A* | CAP**4821AL*+UI & 98(6*B,7MA)60060V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4636 | 2.6831 | 2.6831 | 3.2836 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893522 | HRCU-A-CB | 280ANV024*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)60080V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.5574 | 2.6831 | 2.6831 | 3.0858 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893523 | HRCU-A-CB | 280ANV024*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)66100V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6831 | 2.6831 | 3.3215 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893524 | HRCU-A-CB | 280ANV024*0**A* | CAP**4824AL*+UI & 98(6*B,7MA)60060V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4644 | 2.6831 | 2.6831 | 3.2818 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893525 | HRCU-A-CB | 280ANV024*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)60080V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.7007 | 1.3323 | 1.3323 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.5264 | 2.6831 | 2.6831 | 3.1486 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893526 | HRCU-A-CB | 280ANV024*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)66100V21*** | 24400 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 22800 | 22800 | 0.693 | 1.3177 | 1.3177 | 5.4545 | 5.0698 | 5.0698 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.6536 | 2.6536 | 3.3215 | 2.7383 | 2.7383 |  | 11537.18 |  | 20711.44 | 1.3196 |  | 2.4894 | 2.5617 |  | 2.4377 | 90.84% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893527 | HRCU-A-CB | 280ANV024*0**A* | CAP**6021AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4628 | 2.7126 | 2.7126 | 3.2854 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893528 | HRCU-A-CB | 280ANV024*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.5266 | 2.6831 | 2.6831 | 3.1482 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893529 | HRCU-A-CB | 280ANV024*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.5735 | 2.6831 | 2.6831 | 3.0544 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893530 | HRCU-A-CB | 280ANV024*0**A* | CAP**6024AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 15 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 24800 | 24800 | 1.4469 | 2.7126 | 2.7126 | 3.3215 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893531 | HRCU-A-CB | 280ANV024*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4951 | 2.6831 | 2.6831 | 3.2145 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893532 | HRCU-A-CB | 280ANV024*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 19.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.431 | 2.6831 | 2.6831 | 3.3585 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893533 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3621AL*+UI & 98(6*B,7MA)60060V21*** | 24000 | 14 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7854 | 1.5017 | 1.5017 | 4.912 | 4.5656 | 4.5656 |  | 16740.9 | 25200 | 25200 | 1.5741 | 2.9942 | 2.9942 | 3.1161 | 2.466 | 2.466 |  | 11775.06 |  | 21138.48 | 1.4955 |  | 2.8213 | 2.3069 |  | 2.1953 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893534 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3621AL*+UI & 98(6*B,7*A)60080V21*** | 24000 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7777 | 1.487 | 1.487 | 4.9606 | 4.6108 | 4.6108 |  | 16740.9 | 25200 | 25200 | 1.4767 | 2.9648 | 2.9648 | 3.3215 | 2.4904 | 2.4904 |  | 11775.06 |  | 21138.48 | 1.4809 |  | 2.7937 | 2.3298 |  | 2.217 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893535 | HRCU-A-CB | 280ANV024*0**A* | CNPV*3621AL*+UI & 98(6*B,7*A)66100V21*** | 24000 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7777 | 1.487 | 1.487 | 4.9606 | 4.6108 | 4.6108 |  | 16740.9 | 25200 | 25200 | 1.4767 | 2.9648 | 2.9648 | 3.3215 | 2.4904 | 2.4904 |  | 11775.06 |  | 21138.48 | 1.4809 |  | 2.7937 | 2.3298 |  | 2.217 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893536 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4221AL*+UI & 98(6*B,7MA)60060V21*** | 24400 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7623 | 1.4575 | 1.4575 | 5.0609 | 4.7039 | 4.7039 |  | 16740.9 | 25200 | 25200 | 1.5259 | 2.9061 | 2.9061 | 3.2145 | 2.5407 | 2.5407 |  | 11775.06 |  | 21138.48 | 1.4515 |  | 2.7383 | 2.3768 |  | 2.2618 | 90.34% | 83.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893537 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)60080V21*** | 24400 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7469 | 1.4303 | 1.4303 | 5.113 | 4.7524 | 4.7524 |  | 16571.8 | 25200 | 25200 | 1.4469 | 2.8765 | 2.8765 | 3.3558 | 2.5669 | 2.5669 |  | 11656.12 |  | 20924.96 | 1.4222 |  | 2.683 | 2.4013 |  | 2.2851 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893538 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)66100V21*** | 24400 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7469 | 1.4303 | 1.4303 | 5.113 | 4.7524 | 4.7524 |  | 16571.8 | 25000 | 25000 | 1.5421 | 2.8536 | 2.8536 | 3.1486 | 2.5669 | 2.5669 |  | 11656.12 |  | 20924.96 | 1.4222 |  | 2.683 | 2.4013 |  | 2.2851 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893539 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4824AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.6054 | 2.736 | 2.736 | 3.0244 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893540 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 25000 | 25000 | 1.4469 | 2.7345 | 2.7345 | 3.3215 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893541 | HRCU-A-CB | 280ANV024*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 25000 | 25000 | 1.4951 | 2.7047 | 2.7047 | 3.2145 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893542 | HRCU-A-CB | 280ANV024*0**A* | CNPV*6024AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 23400 | 23400 | 0.7238 | 1.3839 | 1.3839 | 5.3301 | 4.9541 | 4.9541 |  | 16740.9 | 25000 | 25000 | 1.4767 | 2.7375 | 2.7375 | 3.3215 | 2.6758 | 2.6758 |  | 11775.06 |  | 21138.48 | 1.3782 |  | 2.6 | 2.5033 |  | 2.3821 | 90.34% | 84.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893543 | HRCU-A-CB | 280ANV024*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4618 | 2.7066 | 2.7066 | 3.3215 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893544 | HRCU-A-CB | 280ANV024*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 20 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4779 | 2.7066 | 2.7066 | 3.2854 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893545 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7MA)60060V21*** | 24600 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25200 | 25200 | 1.4787 | 2.8172 | 2.8172 | 3.2836 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.3929 |  | 2.6277 | 2.4519 |  | 2.3332 | 90.19% | 83.04% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893546 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)60080V21*** | 24600 | 14.5 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25000 | 25000 | 1.5903 | 2.7948 | 2.7948 | 3.0531 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.3929 |  | 2.6277 | 2.4519 |  | 2.3332 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893547 | HRCU-A-CB | 280ANV024*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)66100V21*** | 24600 | 15 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7315 | 1.4008 | 1.4008 | 5.2207 | 4.8524 | 4.8524 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7948 | 2.7948 | 3.3193 | 2.6209 | 2.6209 |  | 11656.12 |  | 20924.96 | 1.3929 |  | 2.6277 | 2.4519 |  | 2.3332 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893548 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 14.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7161 | 1.3714 | 1.3714 | 5.333 | 4.9568 | 4.9568 |  | 16571.8 | 25000 | 25000 | 1.5582 | 2.736 | 2.736 | 3.1161 | 2.6773 | 2.6773 |  | 11656.12 |  | 20924.96 | 1.3636 |  | 2.5724 | 2.5046 |  | 2.3834 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893549 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4628 | 2.7066 | 2.7066 | 3.3193 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893550 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7084 | 1.3588 | 1.3588 | 5.3359 | 4.9596 | 4.9596 |  | 16402.7 | 25000 | 25000 | 1.5582 | 2.7345 | 2.7345 | 3.0843 | 2.6788 | 2.6788 |  | 11537.18 |  | 20711.44 | 1.3489 |  | 2.5447 | 2.506 |  | 2.3847 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893551 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7MA)60060V21*** | 24800 | 14.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7084 | 1.3566 | 1.3566 | 5.3909 | 5.0107 | 5.0107 |  | 16571.8 | 25000 | 25000 | 1.4469 | 2.7066 | 2.7066 | 3.3558 | 2.7064 | 2.7064 |  | 11656.12 |  | 20924.96 | 1.3489 |  | 2.5447 | 2.5318 |  | 2.4093 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893552 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)60080V21*** | 24800 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 25000 | 25000 | 1.5264 | 2.7047 | 2.7047 | 3.1486 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 82.85% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893553 | HRCU-A-CB | 280ANV024*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)66100V21*** | 24800 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 12901 | 23000 | 23000 | 0.7007 | 1.344 | 1.344 | 5.3945 | 5.0141 | 5.0141 |  | 16402.7 | 24800 | 24800 | 1.4628 | 2.6831 | 2.6831 | 3.2854 | 2.7082 | 2.7082 |  | 11537.18 |  | 20711.44 | 1.3342 |  | 2.5171 | 2.5335 |  | 2.4109 | 90.05% | 83.51% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893554 | HRCU-A-CB | 280ANV024*0**A* | CSPH*6012AL*+UI & 98(6*B,7MA)60060V21*** | 25000 | 15 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4965 | 2.6771 | 2.6771 | 3.2446 | 2.7361 | 2.7361 |  | 11656.12 |  | 20924.96 | 1.3342 |  | 2.5171 | 2.5597 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893555 | HRCU-A-CB | 280ANV024*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)60080V21*** | 25000 | 15 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13034 | 23200 | 23200 | 0.7007 | 1.3419 | 1.3419 | 5.4502 | 5.0657 | 5.0657 |  | 16571.8 | 25000 | 25000 | 1.4618 | 2603 | 2603 | 3.3215 | 2.74 | 2.74 |  | 11656.12 |  | 20924.96 | 1.3342 |  | 2.5171 | 2.5597 |  | 2.4358 | 90.19% | 83.7% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant | Evolution Series | 9893556 | HRCU-A-CB | 280ANV036000 | FE4ANB006L+UI | 35000 | 14.5 | 20.5 | 13 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.07 | 2.07 | 4.1153 | 4.7288 | 4.7288 |  | 13250 | 31600 | 31600 | 1.83 | 3.3 | 3.3 | 2.122 | 2.8064 | 2.8064 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.6633 |  | 2.2027 | 70.66% | 74.68% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893607 | HRCU-A-CB | 280ANV036000 | FE4ANF002L+UI | 33000 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 |  | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.6094 |  | 11310.2 |  | 33496 | 2.1432 |  | 3.5796 | 1.5466 |  | 2.7424 | 94.62% | 109.5% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893608 | HRCU-A-CB | 280ANV036000 | FE4AN(B,F)003L+UI | 33400 | 13 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 14273.8 | 35738 | 35600 | 1.083 | 2.3598 | 2.3598 | 3.8626 | 4.4384 | 4.4213 |  | 14177.5 | 33812 | 30200 | 2.0862 | 3.762 | 3.762 | 1.9917 | 2.6341 | 2.3527 |  | 11416.9 |  | 25252 | 2.1432 |  | 3.5796 | 1.5612 |  | 2.0674 | 70.93% | 83.62% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893614 | HRCU-A-CB | 280ANV036000 | FE4AN(B,F)005L+UI | 35000 | 13.5 | 20 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 1.0165 | 2.2149 | 2.2149 | 3.8461 | 4.4194 | 4.4194 |  | 13250 | 31600 | 31800 | 1.9581 | 3.531 | 3.531 | 1.9831 | 2.6228 | 2.6394 |  | 10670 |  | 23600 | 2.0116 |  | 3.3598 | 1.5545 |  | 2.0586 | 70.66% | 74.21% | N/A |  |  | N/A
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893621 | HRCU-A-CB | 280ANV036*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)66120V24*** | 33600 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13965 | 35000 | 35000 | 0.8547 | 2.4593 | 2.4593 | 4.7873 | 4.1699 | 4.1699 |  | 17745 | 30200 | 30200 | 1.5651 | 3.6853 | 3.6853 | 3.322 | 2.401 | 2.401 |  | 12184.2 |  | 26961.9 | 2.0456 |  | 3.4282 | 1.7452 |  | 2.3044 | 77.03% | 89.28% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893625 | HRCU-A-CB | 280ANV036*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)42080V17*** | 33600 | 12.5 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8393 | 2.4102 | 2.4102 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 32600 | 32600 | 1.5369 | 4.0612 | 4.0612 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0824 |  | 3.4898 | 1.6491 |  | 2.1774 | 77.19% | 79.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893626 | HRCU-A-CB | 280ANV036*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)66120V24*** | 34200 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8085 | 2.3404 | 2.3404 | 4.7717 | 4.1563 | 4.1563 |  | 16731 | 32000 | 32000 | 1.4805 | 3.9177 | 3.9177 | 3.3111 | 2.3932 | 2.3932 |  | 11487.96 |  | 25421.22 | 1.8572 |  | 3.1126 | 1.8123 |  | 2.393 | 76.57% | 79.44% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893628 | HRCU-A-CB | 280ANV036*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)42080V17*** | 34200 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33000 | 33000 | 0.8162 | 2.3485 | 2.3485 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 32000 | 32000 | 1.4946 | 3.955 | 3.955 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.1199 |  | 3.5527 | 1.5878 |  | 2.0965 | 77.03% | 79.44% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893629 | HRCU-A-CB | 280ANV036*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)66120V24*** | 34400 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 32800 | 32800 | 0.8008 | 2.3136 | 2.3136 | 4.7689 | 4.1538 | 4.1538 |  | 16562 | 31600 | 31600 | 1.4664 | 3.871 | 3.871 | 3.3092 | 2.3918 | 2.3918 |  | 11371.92 |  | 25164.44 | 1.8197 |  | 3.0497 | 1.831 |  | 2.4177 | 76.72% | 79.63% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893639 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)42080V17*** | 34000 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.847 | 2.4515 | 2.4515 | 4.6928 | 4.0876 | 4.0876 |  | 17238 | 32600 | 32600 | 1.551 | 4.0583 | 4.0583 | 3.2564 | 2.3536 | 2.3536 |  | 11836.08 |  | 26191.56 | 2.0857 |  | 3.4955 | 1.6627 |  | 2.1954 | 76.58% | 80.34% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893640 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)66120V24*** | 34200 | 13.5 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 32200 | 32200 | 1.5087 | 3.8992 | 3.8992 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 1.8948 |  | 3.1754 | 1.8303 |  | 2.4167 | 77.03% | 81.34% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893641 | HRCU-A-CB | 280ANV036*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66120V24*** | 35000 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8316 | 2.3881 | 2.3881 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32200 | 32200 | 1.5228 | 3.9746 | 3.9746 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 77.19% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893644 | HRCU-A-CB | 280ANV036*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)66120V24*** | 33600 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13965 | 35200 | 35200 | 0.8316 | 2.4065 | 2.4065 | 4.9203 | 4.2857 | 4.2857 |  | 17745 | 30400 | 30400 | 1.5228 | 3.6094 | 3.6094 | 3.4143 | 2.4677 | 2.4677 |  | 12184.2 |  | 26961.9 | 2.0618 |  | 3.4555 | 1.7314 |  | 2.2862 | 76.6% | 88.69% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893646 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)42080V17*** | 33600 | 12.5 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13832 | 34800 | 34800 | 0.8316 | 2.402 | 2.402 | 4.8734 | 4.2449 | 4.2449 |  | 17576 | 30600 | 30600 | 1.5228 | 3.6681 | 3.6681 | 3.3817 | 2.4442 | 2.4442 |  | 12068.16 |  | 26705.12 | 2.0625 |  | 3.4566 | 1.7144 |  | 2.2636 | 76.74% | 87.27% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893647 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)66120V24*** | 33800 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13832 | 34600 | 34600 | 0.8085 | 2.3219 | 2.3219 | 5.0127 | 4.3662 | 4.3662 |  | 17576 | 30200 | 30200 | 1.4805 | 3.5196 | 3.5196 | 3.4784 | 2.5141 | 2.5141 |  | 12068.16 |  | 26705.12 | 2.0261 |  | 3.3955 | 1.7452 |  | 2.3044 | 77.18% | 88.43% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893649 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)42080V17*** | 33600 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8316 | 2.4023 | 2.4023 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32800 | 32800 | 1.5228 | 4.0486 | 4.0486 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 2.0434 |  | 3.4245 | 1.6805 |  | 2.219 | 76.73% | 79.07% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893650 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)66120V24*** | 34000 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8085 | 2.3217 | 2.3217 | 4.8681 | 4.2402 | 4.2402 |  | 17069 | 32200 | 32200 | 1.4805 | 3.8642 | 3.8642 | 3.378 | 2.4415 | 2.4415 |  | 11720.04 |  | 25934.78 | 2.0261 |  | 3.3955 | 1.6949 |  | 2.2379 | 77.19% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893651 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)42060V17*** | 34200 | 12.5 | 18 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8162 | 2.3578 | 2.3578 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32600 | 32600 | 1.5222 | 3.9494 | 3.9494 | 3.2854 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.933 |  | 3.2396 | 1.7764 |  | 2.3456 | 76.73% | 79.55% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893652 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)42080V17*** | 34400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.8162 | 2.3439 | 2.3439 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32400 | 32400 | 1.4946 | 3.9252 | 3.9252 | 3.3462 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.9886 |  | 3.3326 | 1.7268 |  | 2.2801 | 77.19% | 80.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893653 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)66120V24*** | 34600 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13300 | 33400 | 33400 | 0.7931 | 2.2866 | 2.2866 | 4.9135 | 4.2798 | 4.2798 |  | 16900 | 32000 | 32000 | 1.4523 | 3.8047 | 3.8047 | 3.4095 | 2.4643 | 2.4643 |  | 11604 |  | 25678 | 1.9689 |  | 3.2996 | 1.7268 |  | 2.2801 | 76.88% | 80.24% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893654 | HRCU-A-CB | 280ANV036*0**A* | CAP**3621AL*+UI & 98(6*B,7MA)60060V21*** | 33000 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8624 | 2.4814 | 2.4814 | 4.609 | 4.0146 | 4.0146 |  | 17238 | 30600 | 30600 | 1.5792 | 3.8786 | 3.8786 | 3.1983 | 2.3116 | 2.3116 |  | 11836.08 |  | 26191.56 | 2.1261 |  | 3.5632 | 1.6311 |  | 2.1537 | 77.03% | 85.59% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893655 | HRCU-A-CB | 280ANV036*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)60080V21*** | 33400 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8547 | 2.4737 | 2.4737 | 4.6505 | 4.0507 | 4.0507 |  | 17238 | 30400 | 30400 | 1.5651 | 3.8188 | 3.8188 | 3.2271 | 2.3324 | 2.3324 |  | 11836.08 |  | 26191.56 | 2.1011 |  | 3.5213 | 1.6505 |  | 2.1793 | 76.58% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893656 | HRCU-A-CB | 280ANV036*0**A* | CAP**3621AL*+UI & 98(6*B,7*A)66100V21*** | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.847 | 2.4371 | 2.4371 | 4.6928 | 4.0876 | 4.0876 |  | 17238 | 30200 | 30200 | 1.551 | 3.7595 | 3.7595 | 3.2564 | 2.3536 | 2.3536 |  | 11836.08 |  | 26191.56 | 2.0824 |  | 3.4898 | 1.6654 |  | 2.199 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893657 | HRCU-A-CB | 280ANV036*0**A* | CAP**4221AL*+UI & 98(6*B,7MA)60060V21*** | 33200 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 30600 | 30600 | 1.5369 | 3.812 | 3.812 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0556 |  | 3.4451 | 1.6705 |  | 2.2057 | 76.73% | 84.75% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893658 | HRCU-A-CB | 280ANV036*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)60080V21*** | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0651 |  | 3.4609 | 1.6793 |  | 2.2174 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893659 | HRCU-A-CB | 280ANV036*0**A* | CAP**4221AL*+UI & 98(6*B,7*A)66100V21*** | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893660 | HRCU-A-CB | 280ANV036*0**A* | CAP**4224AL*+UI & 98(6*B,7MA)60060V21*** | 33200 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 30400 | 30400 | 1.5369 | 3.7871 | 3.7871 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.003 |  | 3.3569 | 1.7144 |  | 2.2636 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893661 | HRCU-A-CB | 280ANV036*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)60080V21*** | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0651 |  | 3.4609 | 1.6793 |  | 2.2174 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893662 | HRCU-A-CB | 280ANV036*0**A* | CAP**4224AL*+UI & 98(6*B,7*A)66100V21*** | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8239 | 2.3707 | 2.3707 | 4.8244 | 4.2022 | 4.2022 |  | 17238 | 30200 | 30200 | 1.5087 | 3.657 | 3.657 | 3.3477 | 2.4196 | 2.4196 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893663 | HRCU-A-CB | 280ANV036*0**A* | CAP**4821AL*+UI & 98(6*B,7MA)60060V21*** | 33800 | 12.5 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7931 | 2.2775 | 2.2775 | 4.9626 | 4.3226 | 4.3226 |  | 17069 | 30200 | 30200 | 1.4523 | 3.5551 | 3.5551 | 3.4436 | 2.489 | 2.489 |  | 11720.04 |  | 25934.78 | 2.0448 |  | 3.427 | 1.6793 |  | 2.2174 | 77.19% | 85.88% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893664 | HRCU-A-CB | 280ANV036*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)60080V21*** | 34000 | 13 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7854 | 2.2554 | 2.2554 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.9323 |  | 3.2383 | 1.7771 |  | 2.3465 | 77.19% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893665 | HRCU-A-CB | 280ANV036*0**A* | CAP**4821AL*+UI & 98(6*B,7*A)66100V21*** | 34000 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893666 | HRCU-A-CB | 280ANV036*0**A* | CAP**4824AL*+UI & 98(6*B,7MA)60060V21*** | 34000 | 12.5 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13034 | 32800 | 32800 | 0.7777 | 2.2469 | 2.2469 | 4.9105 | 4.2772 | 4.2772 |  | 16562 | 30200 | 30200 | 1.4241 | 3.5928 | 3.5928 | 3.4075 | 2.4628 | 2.4628 |  | 11371.92 |  | 25164.44 | 1.9499 |  | 3.2679 | 1.7088 |  | 2.2563 | 76.72% | 83.33% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893667 | HRCU-A-CB | 280ANV036*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)60080V21*** | 34000 | 13 | 18.5 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9528 |  | 3.2726 | 1.7585 |  | 2.3219 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893668 | HRCU-A-CB | 280ANV036*0**A* | CAP**4824AL*+UI & 98(6*B,7*A)66100V21*** | 34000 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33600 | 33600 | 0.7777 | 2.2333 | 2.2333 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 29800 | 29800 | 1.4241 | 3.4399 | 3.4399 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 77.19% | 87.03% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893669 | HRCU-A-CB | 280ANV036*0**A* | CAP**6021AL*+UI & 98(6*B,7MA)60060V21*** | 34600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8316 | 2.4073 | 2.4073 | 4.6391 | 4.0408 | 4.0408 |  | 16731 | 32200 | 32200 | 1.5228 | 4.0549 | 4.0549 | 3.2192 | 2.3267 | 2.3267 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 78.95% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893670 | HRCU-A-CB | 280ANV036*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)60080V21*** | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.0261 |  | 3.3955 | 1.6613 |  | 2.1936 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893671 | HRCU-A-CB | 280ANV036*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)66100V21*** | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8008 | 2.3182 | 2.3182 | 4.8176 | 4.1962 | 4.1962 |  | 16731 | 31800 | 31800 | 1.4664 | 3.8562 | 3.8562 | 3.343 | 2.4162 | 2.4162 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893672 | HRCU-A-CB | 280ANV036*0**A* | CAP**6024AL*+UI & 98(6*B,7MA)60060V21*** | 34600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8316 | 2.4073 | 2.4073 | 4.6391 | 4.0408 | 4.0408 |  | 16731 | 32200 | 32200 | 1.5228 | 4.0549 | 4.0549 | 3.2192 | 2.3267 | 2.3267 |  | 11487.96 |  | 25421.22 | 1.9709 |  | 3.3031 | 1.7078 |  | 2.2549 | 76.57% | 78.95% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893673 | HRCU-A-CB | 280ANV036*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)60080V21*** | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 2.0261 |  | 3.3955 | 1.6613 |  | 2.1936 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893674 | HRCU-A-CB | 280ANV036*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)66100V21*** | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13167 | 33200 | 33200 | 0.8162 | 2.3627 | 2.3627 | 4.7267 | 4.1171 | 4.1171 |  | 16731 | 31800 | 31800 | 1.4946 | 3.9303 | 3.9303 | 3.2799 | 2.3706 | 2.3706 |  | 11487.96 |  | 25421.22 | 1.9886 |  | 3.3326 | 1.6927 |  | 2.235 | 76.57% | 79.94% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893676 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)60080V21*** | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8393 | 2.4292 | 2.4292 | 4.7359 | 4.1251 | 4.1251 |  | 17238 | 30400 | 30400 | 1.5369 | 3.75 | 3.75 | 3.2863 | 2.3752 | 2.3752 |  | 11836.08 |  | 26191.56 | 2.0681 |  | 3.466 | 1.6768 |  | 2.2141 | 76.58% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893677 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4221AL*+UI & 98(6*B,7*A)66100V21*** | 33600 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34200 | 34200 | 0.8316 | 2.4069 | 2.4069 | 4.7797 | 4.1633 | 4.1633 |  | 17238 | 30200 | 30200 | 1.5228 | 3.6911 | 3.6911 | 3.3167 | 2.3972 | 2.3972 |  | 11836.08 |  | 26191.56 | 2.0448 |  | 3.427 | 1.6959 |  | 2.2393 | 76.58% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893678 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4821AL*+UI & 98(6*B,7MA)60060V21*** | 33800 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 30400 | 30400 | 1.4664 | 3.6134 | 3.6134 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 2.0434 |  | 3.4245 | 1.6805 |  | 2.219 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893679 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)60080V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7854 | 2.2688 | 2.2688 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.951 |  | 3.2698 | 1.7601 |  | 2.324 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893680 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)66100V21*** | 34200 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893681 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4824AL*+UI & 98(6*B,7MA)60060V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30400 | 30400 | 1.4805 | 3.6124 | 3.6124 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893682 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)60080V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7854 | 2.2688 | 2.2688 | 5.0112 | 4.3649 | 4.3649 |  | 17069 | 30000 | 30000 | 1.4382 | 3.4973 | 3.4973 | 3.4774 | 2.5134 | 2.5134 |  | 11720.04 |  | 25934.78 | 1.9505 |  | 3.2688 | 1.7606 |  | 2.3246 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893683 | HRCU-A-CB | 280ANV036*0**A* | CNPV*4824AL*+UI & 98(6*B,7*A)66100V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9135 |  | 3.2069 | 1.7946 |  | 2.3695 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893684 | HRCU-A-CB | 280ANV036*0**A* | CNPV*6024AL*+UI & 98(6*B,7MA)60060V21*** | 34600 | 13 | 19 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8547 | 2.469 | 2.469 | 4.6049 | 4.011 | 4.011 |  | 17069 | 32400 | 32400 | 1.5651 | 4.1103 | 4.1103 | 3.1954 | 2.3096 | 2.3096 |  | 11720.04 |  | 25934.78 | 2.0261 |  | 3.3955 | 1.6949 |  | 2.2379 | 76.73% | 80.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893685 | HRCU-A-CB | 280ANV036*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)60080V21*** | 34800 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8393 | 2.4245 | 2.4245 | 4.6894 | 4.0846 | 4.0846 |  | 17069 | 32200 | 32200 | 1.5369 | 4.0114 | 4.0114 | 3.2541 | 2.3519 | 2.3519 |  | 11720.04 |  | 25934.78 | 2.0824 |  | 3.4898 | 1.6491 |  | 2.1774 | 76.73% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893686 | HRCU-A-CB | 280ANV036*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66100V21*** | 34800 | 13.5 | 19.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8316 | 2.4023 | 2.4023 | 4.7328 | 4.1224 | 4.1224 |  | 17069 | 32000 | 32000 | 1.5228 | 3.9499 | 3.9499 | 3.2842 | 2.3737 | 2.3737 |  | 11720.04 |  | 25934.78 | 2.0448 |  | 3.427 | 1.6793 |  | 2.2174 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893688 | HRCU-A-CB | 280ANV036*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)60080V21*** | 33400 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30200 | 30200 | 1.4805 | 3.5886 | 3.5886 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 2.0073 |  | 3.3641 | 1.7276 |  | 2.2812 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893689 | HRCU-A-CB | 280ANV036*0**A* | CSPH*3612AL*+UI & 98(6*B,7*A)66100V21*** | 33400 | 13 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8008 | 2.3042 | 2.3042 | 4.9635 | 4.3234 | 4.3234 |  | 17238 | 30200 | 30200 | 1.4664 | 3.5544 | 3.5544 | 3.4443 | 2.4894 | 2.4894 |  | 11836.08 |  | 26191.56 | 1.9698 |  | 3.3012 | 1.7606 |  | 2.3246 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893690 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4212AL*+UI & 98(6*B,7MA)60060V21*** | 33400 | 12.5 | 18 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.8085 | 2.3263 | 2.3263 | 4.9163 | 4.2822 | 4.2822 |  | 17238 | 30400 | 30400 | 1.4805 | 3.6124 | 3.6124 | 3.4115 | 2.4657 | 2.4657 |  | 11836.08 |  | 26191.56 | 1.9319 |  | 3.2377 | 1.7951 |  | 2.3702 | 77.03% | 86.16% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893691 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)60080V21*** | 33400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13566 | 34000 | 34000 | 0.7854 | 2.2599 | 2.2599 | 5.0609 | 4.4082 | 4.4082 |  | 17238 | 30200 | 30200 | 1.4382 | 3.4861 | 3.4861 | 3.5118 | 2.5382 | 2.5382 |  | 11836.08 |  | 26191.56 | 1.9698 |  | 3.3012 | 1.7606 |  | 2.3246 | 77.03% | 86.73% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893692 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4212AL*+UI & 98(6*B,7*A)66100V21*** | 33600 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893693 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4812AL*+UI & 98(6*B,7MA)60060V21*** | 33800 | 12.5 | 18.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7931 | 2.2911 | 2.2911 | 4.9626 | 4.3226 | 4.3226 |  | 17069 | 30400 | 30400 | 1.4523 | 3.5787 | 3.5787 | 3.4436 | 2.489 | 2.489 |  | 11720.04 |  | 25934.78 | 1.9698 |  | 3.3012 | 1.7433 |  | 2.3018 | 76.73% | 85.31% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893694 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)60080V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.9323 |  | 3.2383 | 1.7771 |  | 2.3465 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893695 | HRCU-A-CB | 280ANV036*0**A* | CSPH*4812AL*+UI & 98(6*B,7*A)66100V21*** | 34000 | 13 | 19 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.7777 | 2.2466 | 2.2466 | 5.0609 | 4.4082 | 4.4082 |  | 17069 | 30000 | 30000 | 1.4241 | 3.463 | 3.463 | 3.5118 | 2.5382 | 2.5382 |  | 11720.04 |  | 25934.78 | 1.8948 |  | 3.1754 | 1.8123 |  | 2.393 | 76.73% | 86.45% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893696 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7MA)60060V21*** | 34400 | 13 | 18.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8162 | 2.3578 | 2.3578 | 4.8221 | 4.2002 | 4.2002 |  | 17069 | 32200 | 32200 | 1.4946 | 3.901 | 3.901 | 3.3462 | 2.4185 | 2.4185 |  | 11720.04 |  | 25934.78 | 1.9516 |  | 3.2707 | 1.7595 |  | 2.3233 | 76.73% | 80.54% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893697 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)60080V21*** | 34600 | 13 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 32000 | 32000 | 1.4664 | 3.8036 | 3.8036 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 1.9886 |  | 3.3326 | 1.7268 |  | 2.2801 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893698 | HRCU-A-CB | 280ANV036*0**A* | CSPH*6012AL*+UI & 98(6*B,7*A)66100V21*** | 34800 | 13.5 | 19 | 11.5 | Yes | Centrally Ducted | N/A | N/A | 13433 | 33800 | 33800 | 0.8008 | 2.3133 | 2.3133 | 4.9149 | 4.281 | 4.281 |  | 17069 | 32000 | 32000 | 1.4664 | 3.8036 | 3.8036 | 3.4105 | 2.465 | 2.465 |  | 11720.04 |  | 25934.78 | 1.951 |  | 3.2698 | 1.7601 |  | 2.324 | 76.73% | 81.05% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant | Evolution Series | 9893699 | HRCU-A-CB | 280ANV048000 | FE4ANB006L+UI | 47500 | 13.5 | 18 | 12 | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 2.96 | 2.96 | 4.4919 | 4.505 | 4.505 |  | 23840 | 47500 | 47500 | 2.66 | 5.66 | 5.66 | 2.6283 | 2.4595 | 2.4595 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.2101 | #DIV/0! | 2.2449 | 83.67% | 80.15% | N/A |  |  | N/A
Bryant | Bryant | Evolution Series | 9893727 | HRCU-A-CB | 280ANV048000 | FE4AN(B,F)005L+UI | 46500 | 12.5 | 17.5 | 11 | Yes | Centrally Ducted | N/A | N/A | 24800 | 46500 | 46500 | 1.7172 | 3.1968 | 3.1968 | 4.2326 | 4.263 | 4.263 |  | 24300 | 48500 | 48500 | 2.8728 | 6.1128 | 6.1128 | 2.479 | 2.3253 | 2.3253 |  | 19600 |  | 38800 | 2.754 |  | 5.3676 | 2.0858 |  | 2.1185 | 83.44% | 80% | N/A |  |  | N/A
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893731 | HRCU-A-CB | 280ANV048*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66120V24*** | 46500 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25544 | 46000 | 46000 | 1.5606 | 3.2438 | 3.2438 | 4.7958 | 4.155 | 4.155 |  | 30179 | 49000 | 49000 | 2.8968 | 6.4052 | 6.4052 | 3.0525 | 2.2414 | 2.2414 |  | 21541.42 |  | 42258.84 | 2.5057 |  | 5.0735 | 2.5189 |  | 2.4405 | 91.87% | 86.24% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893742 | HRCU-A-CB | 280ANV048*0**A* | CAP**6021AL*+UI & 98(6*B,7*A)66100V21*** | 46000 | 12.5 | 17 | 11 | Yes | Centrally Ducted | N/A | N/A | 25048 | 45500 | 45500 | 1.5453 | 3.24 | 3.24 | 4.7492 | 4.1146 | 4.1146 |  | 29593 | 48000 | 48000 | 2.8684 | 6.336 | 6.336 | 3.0228 | 2.2197 | 2.2197 |  | 21123.14 |  | 41438.28 | 2.4566 |  | 5.0237 | 2.5193 |  | 2.4168 | 91.07% | 86.33% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893745 | HRCU-A-CB | 280ANV048*0**A* | CAP**6024AL*+UI & 98(6*B,7*A)66100V21*** | 46000 | 12.5 | 17 | 11 | Yes | Centrally Ducted | N/A | N/A | 24800 | 45500 | 45500 | 1.6065 | 3.402 | 3.402 | 4.5231 | 3.9187 | 3.9187 |  | 29300 | 48000 | 48000 | 2.982 | 6.6528 | 6.6528 | 2.8789 | 2.114 | 2.114 |  | 20914 |  | 41028 | 2.4327 |  | 5.2227 | 2.5189 |  | 2.3017 | 90.17% | 85.47% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893748 | HRCU-A-CB | 280ANV048*0**A* | CNPV*4821AL*+UI & 98(6*B,7*A)66100V21*** | 45500 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 26040 | 46000 | 46000 | 1.5912 | 3.2444 | 3.2444 | 4.7949 | 4.1542 | 4.1542 |  | 30765 | 48000 | 48000 | 2.9536 | 6.2757 | 6.2757 | 3.0519 | 2.241 | 2.241 |  | 21959.7 |  | 43079.4 | 2.5539 |  | 5.173 | 2.5193 |  | 2.44 | 93.65% | 89.75% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893753 | HRCU-A-CB | 280ANV048*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)60080V21*** | 46000 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25072.8 | 46000 | 46000 | 1.6677 | 3.5316 | 3.5316 | 4.405 | 3.8164 | 3.8164 |  | 29622.3 | 49000 | 49000 | 3.0956 | 6.9734 | 6.9734 | 2.8037 | 2.0588 | 2.0588 |  | 21144.054 |  | 41479.308 | 2.4595 |  | 5.4217 | 2.5189 |  | 2.2416 | 90.17% | 84.65% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant® Heating and Cooling Systems | Bryant® Extreme Heat Pump | 9893754 | HRCU-A-CB | 280ANV048*0**A* | CNPV*6024AL*+UI & 98(6*B,7*A)66100V21*** | 46000 | 12.5 | 17.5 | 10.5 | Yes | Centrally Ducted | N/A | N/A | 25072.8 | 46000 | 46000 | 1.6509 | 3.4959 | 3.4959 | 4.4499 | 3.8553 | 3.8553 |  | 29622.3 | 48500 | 48500 | 3.0644 | 6.8326 | 6.8326 | 2.8323 | 2.0798 | 2.0798 |  | 21144.054 |  | 41479.308 | 2.4595 |  | 5.3669 | 2.5189 |  | 2.2645 | 90.17% | 85.52% | N/A |  |  | N/A | [7 empty] | 2018-01-30
Bryant | Bryant | Evolution Series | 9893760 | HRCU-A-CB | 280ANV060000 | FE4ANB006L+UI | 56000 | 12.5 | 18 | 12 | Yes | Centrally Ducted | N/A | N/A | 24600 | 55500 | 55500 | 1.75 | 4.15 | 4.15 | 4.1197 | 3.9194 | 3.9194 |  | 24160 | 52500 | 52500 | 2.93 | 6.91 | 6.91 | 2.4166 | 2.2267 | 2.2267 |  | 19400 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920038 | HRCU-A-CB-O | MLA009S4S-1P | MWMA009S4-2P | 9000 | 14.5 | 24 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Lennox Industries, Inc. | Lennox | ML-Series | 9920038 | HRCU-A-CB-O | MLA009S4S-1P | MWMA009S4-2P | 9000 | 14.5 | 24 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920040 | HMSV-A-CB | MLA012S4S-1P | ducted indoor units | 11500 | 12.5 | 19 | 10 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 3752 | 12000 | 17021 | 0.189 | 0.961 | 1.692 | 5.818 | 3.6596 | 2.9482 |  | 3292 | 8500 | 12986 | 0.232 | 0.966 | 2.028 | 4.1586 | 2.5788 | 1.8766 |  | 2718 |  | 12341 | 0.205 |  | 2.031 | 3.8857 |  | 1.7808 | 72.5% | 95.03% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920041 | HRCU-A-CB-O | MLA012S4S-1P | MWMA012S4-2P | 12000 | 12.5 | 22 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Lennox Industries, Inc. | Lennox | ML-Series | 9920041 | HRCU-A-CB-O | MLA012S4S-1P | MWMA012S4-2P | 12000 | 12.5 | 22 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920047 | HRCU-A-CB-O | MLA024S4S-1P | MWMA024S4-2P | 24000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Lennox Industries, Inc. | Lennox | ML-Series | 9920047 | HRCU-A-CB-O | MLA024S4S-1P | MWMA024S4-2P | 24000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920054 | HMSV-A-CB | MLA030S4M-1P | Non-Ducted Indoor Units | 28000 | 13 | 22 | 10.4 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5820 | 28000 | 37720 | 0.895 | 2.345 | 3.475 | 1.9058 | 3.4994 | 3.1812 |  | 5411 | 18000 | 31054 | 0.924 | 1.925 | 4.176 | 1.7162 | 2.7404 | 2.1794 |  | 5145 |  | 28160 | 1.008 |  | 4.041 | 1.4959 |  | 2.0423 | 74.66% | 90.68% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920055 | HMSV-A-CB | MLA036S4M-1P | Non-Ducted Indoor Units | 36000 | 13.5 | 21.5 | 10.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50350 | 1.02 | 2.777 | 4.64 | 2.0716 | 3.7993 | 3.1802 |  | 6845 | 23200 | 38125 | 1.091 | 2.446 | 5.502 | 1.8387 | 2.7797 | 2.0308 |  | 6425 |  | 36000 | 1.146 |  | 5.379 | 1.6431 |  | 1.9614 | 71.5% | 94.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9944775 | HRCU-A-CB-O | GWH09YD-D3DNA1A/O | GWH09AAD-D3DN***/I | 9000 | 16.5 | 38 | 15 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14611 | 0.37 | 0.75 | 1.78 | 2.8079 | 2.1883 | 2.4057 |  | 1745 |  | 12977 | 0.28 |  | 1.82 | 1.8265 |  | 2.0897 | 95.42% | 88.82% | N/A |  |  | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9944776 | HRCU-A-CB-O | GWH12YD-D3DNA1A/O | GWH12AAD-D3DN***/I | 12000 | 15.3 | 30.5 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | N/A |  |  | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962873 | HRCU-A-CB-O | MPA009S4S-1P | MWMA009S4-2P | 9000 | 14.5 | 23.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3102 | 10000 | 11800 | 0.153 | 0.801 | 1.308 | 5.9419 | 3.6588 | 2.6439 |  | 2388 | 5700 | 8678 | 0.178 | 0.702 | 1.098 | 3.9318 | 2.3796 | 2.3163 |  | 2173 |  | 6291 | 0.167 |  | 0.884 | 3.8134 |  | 2.0856 | 53.31% | 72.49% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962874 | HRCU-A-CB-O | MPA012S4S-1P | MWMA012S4-2P | 12000 | 13 | 21.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3820 | 12000 | 16500 | 0.182 | 1.047 | 1.71 | 6.1513 | 3.359 | 2.8279 |  | 3224 | 7600 | 11920 | 0.226 | 0.844 | 1.484 | 4.1808 | 2.639 | 2.354 |  | 2674 |  | 6292 | 0.196 |  | 0.98 | 3.9983 |  | 1.8816 | 38.13% | 52.79% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962876 | HRCU-A-CB-O | MPA024S4S-1P | MWMA024S4-2P | 23000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7060 | 25000 | 31850 | 0.446 | 2.275 | 3.42 | 4.6392 | 3.2206 | 2.7293 |  | 5597 | 17800 | 18825 | 0.532 | 1.877 | 2.461 | 3.0833 | 2.7793 | 2.2418 |  | 4942 |  | 16382 | 0.483 |  | 2.202 | 2.9987 |  | 2.1803 | 51.43% | 87.02% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962880 | HRCU-A-CB-O | MPA012S4S-1P | M22A012S4-2P | 12000 | 13 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4062 | 12000 | 16916 | 0.195 | 0.93 | 1.702 | 6.1049 | 3.7816 | 2.9128 |  | 7200 | 3178 | 11696 | 0.799 | 0.229 | 1.498 | 2.6409 | 4.0672 | 2.2882 |  | 2716 |  | 7465 | 0.218 |  | 1.143 | 3.6513 |  | 1.9141 | 44.13% | 63.83% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 9966569 | HRCU-A-CB-O | RX09QMVJU | FFQ09Q2VJU | 9100 | 13 | 20.9 | 11.7 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 4600 | 10000 | 14000 | 0.25 | 0.64 | 1.15 | 5.4 | 4.59 | 3.57 |  | 3150 | 5830 | 8150 | 0.22 | 0.45 | 0.81 | 4.18 | 3.8 | 2.94 |  | 2420 |  | 6270 | 0.21 |  | 0.76 | 3.38 |  | 2.42 | 44.79% | 76.93% | accessory (KEH067A41E) | 140 | Temp below 23 degrees | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 9966684 | HRCU-A-CB-O | RX12QMVJU | FFQ12Q2VJU | 10800 | 12.5 | 20.2 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 4600 | 13500 | 16800 | 0.25 | 0.99 | 1.45 | 5.4 | 4.02 | 3.39 |  | 3150 | 7850 | 9760 | 0.22 | 0.7 | 1.03 | 4.18 | 3.28 | 2.76 |  | 2420 |  | 7500 | 0.21 |  | 0.96 | 3.38 |  | 2.28 | 44.64% | 76.84% | accessory (KEH067A41E) | 140 | Temp. below 23 degrees | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 9966775 | HRCU-A-CB-O | RX15QMVJU | FFQ15Q2VJU | 14400 | 12.5 | 20.7 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 5200 | 16200 | 16300 | 0.31 | 1.24 | 1.3 | 4.916 | 3.8288 | 3.6747 |  | 3570 | 9400 | 9460 | 0.27 | 0.87 | 0.92 | 3.8751 | 3.1665 | 3.0135 |  | 2740 |  | 7270 | 0.26 |  | 0.86 | 3.08 |  | 2.47 | 44.6% | 76.85% | accessory (KEH063A4E) | 140 | Temp below 23 degrees | N/A
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966837 | HRCU-A-CB-O | BMS500-AAS009-0CSXXA | BMS500-AAU009-0AHXXA | 9000 | 14 | 22 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3580 | 9800 | 12490 | 0.162 | 0.892 | 1.045 | 6.4765 | 3.2198 | 3.5028 |  | 2860 | 5800 | 7868 | 0.175 | 0.625 | 0.962 | 4.7896 | 2.7197 | 2.397 |  | 2513 |  | 6516 | 0.164 |  | 0.933 | 4.4908 |  | 2.0468 | 52.17% | 82.82% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966838 | HRCU-A-CB-O | BMS500-AAS009-1CSXXA | BMS500-AAU009-1AHXXA | 9000 | 14 | 20.5 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3530 | 9800 | 13080 | 0.161 | 0.898 | 1.075 | 6.4257 | 3.1983 | 3.5659 |  | 2610 | 6300 | 8111 | 0.172 | 0.689 | 1.017 | 4.4472 | 2.6797 | 2.3374 |  | 2489 |  | 6609 | 0.159 |  | 1.01 | 4.5878 |  | 1.9177 | 50.53% | 81.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966839 | HRCU-A-CB-O | BMS500-AAS012-0CSXXA | BMS500-AAU012-0AHXXA | 12000 | 12.5 | 20.9 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3680 | 12000 | 12450 | 0.172 | 1.157 | 1.049 | 6.2704 | 3.0396 | 3.4783 |  | 2958 | 7500 | 7360 | 0.182 | 0.865 | 0.909 | 4.7632 | 2.5411 | 2.3729 |  | 2582 |  | 5736 | 0.18 |  | 0.831 | 4.2039 |  | 2.0229 | 46.07% | 77.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966843 | HRCU-A-CB-O | BMS500-AAS018-1CSXXA | BMS500-AAU018-1AHXXA | 18000 | 13 | 22 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4670 | 18000 | 19190 | 0.231 | 1.669 | 1.674 | 5.9249 | 3.1607 | 3.3596 |  | 3920 | 11100 | 13730 | 0.262 | 1.179 | 1.615 | 4.3849 | 2.7592 | 2.4916 |  | 3274 |  | 12524 | 0.251 |  | 2.087 | 3.8228 |  | 1.7587 | 65.26% | 91.22% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966844 | HRCU-A-CB-O | BMS500-AAS024-1CSXXA | BMS500-AAU024-1AHXXA | 24000 | 12.5 | 20 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7200 | 25000 | 29140 | 0.36 | 2.459 | 2.603 | 5.8614 | 2.9796 | 3.2809 |  | 5690 | 16000 | 18650 | 0.486 | 1.906 | 2.478 | 3.4312 | 2.4602 | 2.2057 |  | 5122 |  | 15815 | 0.471 |  | 2.635 | 3.1871 |  | 1.759 | 54.27% | 84.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10053547 | HRCU-A-CB-O | PUZ-A24NHA7 | PLA-A24EA7 | 24000 | 14.3 | 24.2 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 9000 | 26000 | 29000 | 0.45 | 1.75 | 2.07 | 5.8614 | 4.3542 | 4.1058 |  | 5100 | 14900 | 16600 | 0.42 | 1.6 | 1.9 | 3.5587 | 2.7292 | 2.5605 |  | 4500 |  | 13000 | 0.4 |  | 1.4 | 3.297 |  | 2.7214 | 44.83% | 95.24% | N/A |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10054648 | HRCU-A-CB-O | PUZ-A36NKA7 | PLA-A36EA7 | 36000 | 12.9 | 21.8 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 18000 | 38000 | 42000 | 0.94 | 3.54 | 3.02 | 5.612 | 3.146 | 4.0758 |  | 10000 | 22000 | 24000 | 0.93 | 2.49 | 3 | 3.1513 | 2.5894 | 2.3446 |  | 9200 |  | 21600 | 0.83 |  | 2.6 | 3.2485 |  | 2.4347 | 51.43% | 89.25% | N/A |  |  | N/A
Carrier | Bryant |  | 10056158 | HRCU-A-CB | 38MAQB18R--3 | 40MBDQ18---3 | 16500 | 12.5 | 19.9 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 19000 | 19000 | 0.38842 | 1.9005 | 1.7348 | 4.15 | 2.93 | 3.21 |  | 5500 | 13400 | 20200 | 0.5069 | 1.4492 | 2.7665 | 3.18 | 2.71 | 2.14 |  | 5500 |  | 19000 | 0.67729 |  | 3.182 | 2.38 |  | 1.75 | 100% | 94.06% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant |  | 10056159 | HRCU-A-CB | 38MAQB24R--3 | 40MBDQ24---3 | 24000 | 12.5 | 20.5 | 12.5 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 6000 | 24000 | 29250 | 0.42373 | 1.8414 | 2.7389 | 4.15 | 3.82 | 3.13 | 6000 | 6000 | 17300 | 25400 | 0.55299 | 1.9806 | 3.4787 | 3.18 | 2.56 | 2.14 | 6000 | 6000 |  | 24000 | 0.73887 |  | 3.8437 | 2.38 |  | 1.83 | 82.05% | 94.49% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Bryant |  | 10056166 | HRCU-A-CB-O | 38MAQB18R--3 | 40MBCQ18---3 | 16000 | 12.5 | 20 | 10.5 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056167 | HRCU-A-CB-O | MPB009S4S-1L | MWMB009S4-1L | 9500 | 15 | 24.5 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3550 | 11000 | 14500 | 0.151 | 0.862 | 1.65 | 6.8901 | 3.7399 | 2.5755 |  | 2840 | 6500 | 10150 | 0.181 | 0.676 | 1.38 | 4.5985 | 2.818 | 2.1556 |  | 2485 |  | 6776 | 0.16308 |  | 1.02 | 4.4658 |  | 1.9469 | 46.73% | 66.76% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056168 | HRCU-A-CB-O | MPB012S4S-1L | MWMB012S4-1L | 12000 | 13 | 22 | 10.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3690 | 12000 | 16600 | 0.17 | 1.028 | 1.74 | 6.3614 | 3.4211 | 2.796 |  | 2952 | 7600 | 11220 | 0.204 | 0.857 | 1.421 | 4.2409 | 2.599 | 2.314 |  | 2583 |  | 6885 | 0.1836 |  | 1.006 | 4.1231 |  | 2.0058 | 41.48% | 61.36% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056169 | HRCU-A-CB-O | MPB009S4S-1P | MWMA009S4-1P | 9000 | 14.9 | 23.5 | 10.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 12700 | 0.144 | 0.756 | 1.33 | 6.124 | 3.7991 | 2.7985 |  | 2407 | 5800 | 8890 | 0.173 | 0.616 | 1.098 | 4.0776 | 2.7594 | 2.3729 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 62.91% | 89.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056170 | HRCU-A-CB-O | MPB009S4S-1P | MWMA009S4-2P | 9000 | 14.9 | 23.5 | 10.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 12700 | 0.144 | 0.756 | 1.33 | 6.124 | 3.7991 | 2.7985 |  | 2407 | 5800 | 8890 | 0.173 | 0.616 | 1.098 | 4.0776 | 2.7594 | 2.3729 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 62.91% | 89.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056171 | HRCU-A-CB-O | MPB012S4S-1P | MWMA012S4-1P | 12000 | 13.7 | 22.7 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 17300 | 0.177 | 0.999 | 1.68 | 6.4244 | 3.5204 | 3.0179 |  | 3104 | 7700 | 12110 | 0.212 | 0.816 | 1.414 | 4.291 | 2.7655 | 2.51 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 52.8% | 75.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056172 | HRCU-A-CB-O | MPB012S4S-1P | MWMA012S4-2P | 12000 | 13.7 | 22.7 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 17300 | 0.177 | 0.999 | 1.68 | 6.4244 | 3.5204 | 3.0179 |  | 3104 | 7700 | 12110 | 0.212 | 0.816 | 1.414 | 4.291 | 2.7655 | 2.51 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 52.8% | 75.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056173 | HRCU-A-CB-O | MPB018S4S-1P | MWMA018S4-1P | 18000 | 13 | 21 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 23000 | 0.231 | 1.589 | 2.4 | 6.1786 | 3.3199 | 2.8086 |  | 3896 | 11400 | 15120 | 0.277 | 1.228 | 1.723 | 4.122 | 2.7207 | 2.5718 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 48.6% | 73.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056174 | HRCU-A-CB-O | MPB018S4S-1P | MWMA018S4-2P | 18000 | 13 | 21 | 10.4 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 23000 | 0.231 | 1.589 | 2.4 | 6.1786 | 3.3199 | 2.8086 |  | 3896 | 11400 | 15120 | 0.277 | 1.228 | 1.723 | 4.122 | 2.7207 | 2.5718 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 48.6% | 73.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056175 | HRCU-A-CB-O | MPB024S4S-1P | MWMA024S4-1P | 24000 | 13.7 | 20.7 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 32890 | 0.44 | 1.959 | 3.35 | 4.7291 | 3.7401 | 2.8773 |  | 5680 | 15300 | 18925 | 0.528 | 1.661 | 2.618 | 3.1527 | 2.6996 | 2.1186 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 55.03% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056176 | HRCU-A-CB-O | MPB024S4S-1P | MWMA024S4-2P | 24000 | 13.7 | 20.7 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 32890 | 0.44 | 1.959 | 3.35 | 4.7291 | 3.7401 | 2.8773 |  | 5680 | 15300 | 18925 | 0.528 | 1.661 | 2.618 | 3.1527 | 2.6996 | 2.1186 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 55.03% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058816 | HMSV-A-CB | MPB009S4S-1P | ducted indoor units | 9000 | 13.5 | 19.5 | 10.5 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 3056 | 10000 | 12764 | 0.166 | 0.718 | 1.342 | 5.3953 | 4.0818 | 2.7875 |  | 2588 | 6200 | 8991 | 0.176 | 0.64 | 1.212 | 4.3095 | 2.8391 | 2.1741 |  | 2312 |  | 8071 | 0.164 |  | 1.18 | 4.1316 |  | 2.0046 | 63.23% | 89.77% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058821 | HMSV-A-CB | MPB024S4S-1P | ducted indoor units | 24000 | 12.5 | 20 | 10.5 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 7020 | 24400 | 32812 | 0.452 | 1.986 | 3.376 | 4.5517 | 3.6007 | 2.8484 |  | 5862 | 16800 | 18826 | 0.541 | 1.851 | 2.731 | 3.1756 | 2.66 | 2.0203 |  | 5028 |  | 15682 | 0.491 |  | 2.498 | 3.0011 |  | 1.8398 | 47.79% | 83.3% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058825 | HRCU-A-CB-O | MPB018S4S-1P | MCFB018S4-2P | 18000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4826 | 18000 | 23011 | 0.238 | 1.552 | 2.425 | 5.9427 | 3.399 | 2.781 |  | 3964 | 12000 | 14923 | 0.282 | 1.303 | 1.831 | 4.1196 | 2.699 | 2.3886 |  | 3423 |  | 10274 | 0.253 |  | 1.433 | 3.9651 |  | 2.1012 | 44.65% | 68.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058826 | HRCU-A-CB-O | MPB024S4S-1P | MCFA024S4-1P | 24000 | 12.5 | 20 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 32821 | 0.448 | 1.733 | 3.368 | 4.5805 | 4.0587 | 2.856 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 53.94% | 97.21% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058827 | HRCU-A-CB-O | MPB024S4S-1P | MCFA024S4-2P | 24000 | 12.5 | 20 | 11 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 32821 | 0.448 | 1.733 | 3.368 | 4.5805 | 4.0587 | 2.856 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 53.94% | 97.21% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058830 | HRCU-A-CB-O | MPB009S4S-1P | M22A009S4-1P | 9000 | 13 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058831 | HRCU-A-CB-O | MPB009S4S-1P | M22A009S4-2P | 9000 | 13 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058832 | HRCU-A-CB-O | MPB012S4S-1P | M22A012S4-1P | 12000 | 14 | 21.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 17120 | 0.181 | 0.902 | 1.694 | 6.2873 | 3.8989 | 2.9619 |  | 3086 | 7500 | 12012 | 0.219 | 0.82 | 1.523 | 4.1298 | 2.6805 | 2.3115 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 49.43% | 70.45% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058833 | HRCU-A-CB-O | MPB012S4S-1P | M22A012S4-2P | 12000 | 14 | 21.5 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 17120 | 0.181 | 0.902 | 1.694 | 6.2873 | 3.8989 | 2.9619 |  | 3086 | 7500 | 12012 | 0.219 | 0.82 | 1.523 | 4.1298 | 2.6805 | 2.3115 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 49.43% | 70.45% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058834 | HRCU-A-CB-O | MPB018S4S-1P | M22A018S4-1P | 18000 | 12.5 | 20 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 22688 | 0.244 | 1.499 | 2.412 | 5.8794 | 3.5192 | 2.7567 |  | 3931 | 12000 | 15213 | 0.282 | 1.274 | 1.899 | 4.0853 | 2.7605 | 2.3478 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 41.48% | 61.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058835 | HRCU-A-CB-O | MPB018S4S-1P | M22A018S4-2P | 18000 | 12.5 | 20 | 10.3 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 22688 | 0.244 | 1.499 | 2.412 | 5.8794 | 3.5192 | 2.7567 |  | 3931 | 12000 | 15213 | 0.282 | 1.274 | 1.899 | 4.0853 | 2.7605 | 2.3478 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 41.48% | 61.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058836 | HRCU-A-CB-O | MPB024S4S-1P | M33A024S4-1P | 24000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 32546 | 0.448 | 2.043 | 3.368 | 4.6119 | 3.5002 | 2.832 |  | 5712 | 15800 | 18628 | 0.541 | 1.809 | 2.639 | 3.0943 | 2.5597 | 2.0687 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 47.09% | 82.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058836 | HRCU-A-CB-O | MPB024S4S-1P | M33A024S4-2P | 24000 | 12.5 | 20 | 10.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 32546 | 0.448 | 2.043 | 3.368 | 4.6119 | 3.5002 | 2.832 |  | 5712 | 15800 | 18628 | 0.541 | 1.809 | 2.639 | 3.0943 | 2.5597 | 2.0687 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 47.09% | 82.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062010 | HMSV-A-CB | MPB018S4M-1P | Non-Ducted Indoor Units | 18000 | 12.5 | 22.5 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 24480 | 0.52 | 1.547 | 1.98 | 3.2463 | 3.5995 | 3.6234 |  | 5376 | 12000 | 16234 | 0.566 | 1.256 | 2.15 | 2.7837 | 2.8 | 2.2129 |  | 4752 |  | 9662 | 0.581 |  | 1.524 | 2.397 |  | 1.858 | 39.47% | 59.52% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062012 | HMSV-A-CB | MPB030S4M-1P | Non-Ducted Indoor Units | 28000 | 12.5 | 23 | 10.3 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 28000 | 36180 | 0.715 | 2.104 | 3.17 | 2.4634 | 3.9002 | 3.3449 |  | 5721 | 17200 | 24345 | 0.765 | 1.788 | 3.451 | 2.1917 | 2.8193 | 2.0675 |  | 5556 |  | 16820 | 0.843 |  | 2.526 | 1.9316 |  | 1.9515 | 46.49% | 69.09% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062016 | HMSV-A-CB | MPB048S4M-1P | Non-Ducted Indoor Units | 48000 | 12.5 | 22.4 | 10.2 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55820 | 1.02 | 3.908 | 4.705 | 2.0716 | 3.5996 | 3.477 |  | 6822 | 29600 | 36673 | 1.081 | 3.213 | 4.567 | 1.8495 | 2.6999 | 2.3534 |  | 6567 |  | 24120 | 1.115 |  | 3.938 | 1.7261 |  | 1.795 | 43.21% | 65.77% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062018 | HRCU-A-CB-O | TW09HQ3D6DO | TW09HQ3D6DI | 9000 | 16.5 | 38 | 15 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12976.6 | 0.28 |  | 1.8216 | 1.8265 |  | 2.0878 | 95.42% | 88.82% | Integrated | 72 | Heater on below 34°F | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062018 | HRCU-A-CB-O | TW09HQ3D6DO | TW09HQ3D6DI | 9000 | 16.5 | 38 | 15 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12976.6 | 0.28 |  | 1.8216 | 1.8265 |  | 2.0878 | 95.42% | 88.82% | Integrated | 72 | Heater on below 34°F | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062019 | HRCU-A-CB-O | TW12HQ3D6DO | TW12HQ3D6DI | 12000 | 15.3 | 30.5 | 14 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | Integrated | 72 | Heater on below 34°F | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062019 | HRCU-A-CB-O | TW12HQ3D6DO | TW12HQ3D6DI | 12000 | 15.3 | 30.5 | 14 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | Integrated | 72 | Heater on below 34°F | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062020 | HRCU-A-CB-O | TW18HQ3D6DO | TW18HQ3D6DI | 18000 | 13.5 | 24.5 | 12 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.5718 | 3.5169 | 2.309 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.4979 | 2.8297 | 2.1064 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.4192 |  | 2.0326 | 82.69% | 93.48% | Interated | 160 | Heater on below 32°F during compressor operation only. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062020 | HRCU-A-CB-O | TW18HQ3D6DO | TW18HQ3D6DI | 18000 | 13.5 | 24.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.57 | 3.52 | 2.31 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.5 | 2.83 | 2.11 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.42 |  | 2.03 | 82.69% | 93.48% | Integrated | 160 | Under heating mode, the compressor in opening condition, while the outdoor ambient temperature ia below 0 ℃, the chassis heating begin to work. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062021 | HRCU-A-CB-O | TW24HQ3D6DO | TW24HQ3D6DI | 22000 | 13 | 21.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2446 | 3.517 | 2.5348 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6377 | 2.9377 | 2.2773 |  | 4000 |  | 22553.32 | 0.6 |  | 3.2 | 1.9539 |  | 2.0656 | 70.48% | 85.87% | Integrated | 160 | If T outer ring is less than T chassis electric heating open temperature, then the chassis electric heating work； | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062021 | HRCU-A-CB-O | TW24HQ3D6DO | TW24HQ3D6DI | 24000 | 13 | 21.5 | 12 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5347 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6376 | 2.9376 | 2.2772 |  | 4000 |  | 22553.32 | 0.6 |  | 3.2 | 1.9538 |  | 2.0655 | 70.48% | 85.87% | Integrated | 160 | Heater on below 32°F during compressor operation only. | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064019 | HMSV-A-CB | TM24H4O | Non-Ducted Indoor Units | 24000 | 12.5 | 21 | 11 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 7500 | 29000 | 35000 | 0.95 | 2.32 | 4.55 | 2.3137 | 3.6634 | 2.2544 |  | 17900 | 18800 | 23000 | 1.96 | 2 | 2.23 | 2.6765 | 2.7549 | 3.0227 |  | 17800 |  | 18356 | 2.79 |  | 2.97 | 1.8698 |  | 1.8113 | 52.45% | 79.81% | Integrated | 160 | Heater on at or below 34°F, during defrost only | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064021 | HMSV-A-CB | TM30H4O | Non-Ducted Indoor Units | 28400 | 12.5 | 21 | 11.5 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 8189 | 30000 | 32414 | 1.05 | 2.35 | 2.65 | 2.2857 | 3.7413 | 3.5848 |  | 17800 | 18100 | 24000 | 1.98 | 2.03 | 2.25 | 2.6347 | 2.6131 | 3.1261 |  | 18800 |  | 19356 | 2.89 |  | 3.01 | 1.9065 |  | 1.8846 | 59.71% | 80.65% | Integrated | 96 | Heater on at or below 34°F, during defrost only | N/A
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064023 | HMSV-A-CB | TM36H4O | Non-Ducted Indoor Units | 34000 | 12.5 | 21 | 11.5 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 8871 | 42500 | 44356 | 1.25 | 3.37 | 3.6 | 2.0799 | 3.696 | 3.611 |  | 19800 | 26500 | 27500 | 2.01 | 2.7 | 2.95 | 2.887 | 2.8764 | 2.732 |  | 20800 |  | 21356 | 2.99 |  | 3.12 | 2.0388 |  | 2.006 | 48.15% | 77.66% | Integrated | 96 | Heater on at or below 34°F, during defrost only | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10091325 | HMSV-A-CB | MXZ-2C20NA2 | Non-ducted | 18000 | 12.7 | 20 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7400 | 22000 | 25500 | 0.67 | 1.641 | 2.455 | 3.2369 | 3.929 | 3.0441 |  | 12500 | 12500 | 15500 | 1.5 | 1.3 | 1.75 | 2.4423 | 2.818 | 2.5958 |  | 10500 |  | 11100 | 1 |  | 1.6 | 3.0772 |  | 2.0332 | 43.53% | 66.67% | MAC-646BH-E | 120 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10093446 | HRCU-A-CB | 4A6V0024A1 | TAM9A0B30V31 | 24200 | 13.75 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20200 | 21300 | 0.54 | 2.6 | 1.51 | 4.34 | 2.2764 | 4.14 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 60.66% | 75.56% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10093447 | HRCU-A-CB | 4A6V0036A1 | TAM9A0B30V31 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 21300 | 0.54 | 2.42 | 1.6 | 4.66 | 3.947 | 3.9 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 94.93% | 76.02% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10093448 | HRCU-A-CB | 4A6V0036A1 | TAM9A0C36V31 | 35000 | 13.5 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33400 | 21600 | 0.52 | 2.38 | 1.55 | 4.78 | 4.1118 | 4.08 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 91.94% | 76.09% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10093449 | HRCU-A-CB | 4A6V0036A1 | TAM9A0C42V41 | 35600 | 13.5 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33600 | 21400 | 0.51 | 2.2 | 1.57 | 4.82 | 4.4749 | 4 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 90.84% | 77.14% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10093452 | HRCU-A-CB | 4A6V0048A1 | TAM9A0C60V51 | 46500 | 12.5 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 12000 | 43000 | 42700 | 0.78 | 2.26 | 3.56 | 4.5 | 5.5747 | 3.52 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 65.9% | 77.95% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093454 | HRCU-A-CB | 4A6V8024A1 | TAM9A0B30V31 | 23800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20000 | 21000 | 0.54 | 2.6 | 1.55 | 4.34 | 2.2538 | 3.96 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 61.52% | 75.56% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093455 | HRCU-A-CB | 4A6V8024A1 | TAM9A0C36V31 | 24000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 21000 | 21400 | 0.54 | 2.52 | 1.52 | 4.34 | 2.4416 | 4.12 |  | 11320 | 16900 | 16900 | 1.23 | 2.52 | 1.96 | 2.7 | 1.9649 | 2.52 |  | 10830 |  | 12780 | 1.64 |  | 1.9 | 1.94 |  | 1.95 | 59.72% | 75.62% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093456 | HRCU-A-CB | 4A6V8036A1 | TAM9A0B30V31 | 34400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 43900 | 0.53 | 2.4 | 3.45 | 4.64 | 3.9066 | 3.72 |  | 16370 | 26600 | 26800 | 1.84 | 2.4 | 3.27 | 2.6 | 3.2474 | 2.4 |  | 17340 |  | 20760 | 2.6 |  | 3.12 | 1.96 |  | 1.95 | 47.29% | 77.46% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093457 | HRCU-A-CB | 4A6V8036A1 | TAM9A0C36V31 | 35000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32200 | 43400 | 0.52 | 2.36 | 3.36 | 4.68 | 3.9977 | 3.78 |  | 16260 | 26200 | 26400 | 1.85 | 2.36 | 3.27 | 2.58 | 3.2528 | 2.36 |  | 17134 |  | 20500 | 2.64 |  | 3.14 | 1.90 |  | 1.90 | 47.24% | 77.65% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093458 | HRCU-A-CB | 4A6V8036A1 | TAM9A0C42V41 | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30000 | 43200 | 0.51 | 2.22 | 3.43 | 4.82 | 3.9594 | 3.7 |  | 16040 | 25400 | 25700 | 1.91 | 2.22 | 3.39 | 2.46 | 3.3523 | 2.22 |  | 16894 |  | 20040 | 2.72 |  | 3.24 | 1.82 |  | 1.80 | 46.39% | 77.98% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093459 | HRCU-A-CB | 4A6V8037A1 | TAM9A0B30V31 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 31400 | 0.54 | 2.42 | 2.37 | 4.66 | 3.947 | 3.88 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 64.39% | 76.02% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093460 | HRCU-A-CB | 4A6V8037A1 | TAM9A0C36V31 | 35800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 32800 | 32200 | 0.52 | 2.38 | 2.3 | 4.78 | 4.0379 | 4.1 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 61.68% | 76.09% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093461 | HRCU-A-CB | 4A6V8037A1 | TAM9A0C42V41 | 46500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30800 | 33300 | 0.51 | 2.2 | 2.68 | 4.82 | 4.102 | 3.64 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 58.38% | 77.14% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093462 | HRCU-A-CB | 4A6V8048A1 | TAM9A0C42V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12300 | 41500 | 42600 | 0.76 | 2.14 | 3.8 | 4.74 | 5.682 | 3.28 |  | 23290 | 36200 | 36600 | 2.81 | 2.14 | 5 | 2.42 | 4.9563 | 2.14 |  | 24456 |  | 28920 | 4.04 |  | 4.8 | 1.78 |  | 1.75 | 67.89% | 79.02% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093463 | HRCU-A-CB | 4A6V8048A1 | TAM9A0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41000 | 43000 | 0.76 | 2.36 | 3.46 | 4.58 | 5.0902 | 3.64 |  | 22960 | 36400 | 36800 | 2.59 | 2.36 | 4.57 | 2.6 | 4.5191 | 2.36 |  | 24190 |  | 28780 | 3.68 |  | 4.38 | 1.92 |  | 1.95 | 66.93% | 78.21% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093464 | HRCU-A-CB | 4A6V8048A1 | TAM9A0C60V51 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41500 | 42600 | 0.77 | 2.32 | 3.54 | 4.52 | 5.2411 | 3.52 |  | 22850 | 36200 | 36600 | 2.62 | 2.32 | 4.64 | 2.56 | 4.5718 | 2.32 |  | 24150 |  | 28680 | 3.72 |  | 4.42 | 1.90 |  | 1.90 | 67.32% | 78.36% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093467 | HRCU-A-CB | 4A6V8049A1 | TAM9A0C60V51 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12000 | 41000 | 31700 | 0.78 | 2.26 | 2.5 | 4.5 | 5.3154 | 3.72 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 88.77% | 77.95% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10093468 | HRCU-A-CB | 4A6V8060A1 | TAM9A0C60V51 | 54000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 18400 | 50500 | 32300 | 1.21 | 2.1 | 2.55 | 4.46 | 7.0459 | 3.72 |  | 33510 | 49500 | 51100 | 3.94 | 2.1 | 7.14 | 2.5 | 6.9064 | 2.1 |  | 34860 |  | 40780 | 5.6 |  | 6.76 | 1.82 |  | 1.75 | 126.3% | 79.8% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10093494 | HRCU-A-CB | 4TWV0024A1 | TAM9A0B30V31 | 24200 | 13.75 | 19.25 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20200 | 21300 | 0.54 | 2.6 | 1.51 | 4.34 | 2.2764 | 4.14 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 60.66% | 75.56% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10093495 | HRCU-A-CB | 4TWV0036A1 | TAM9A0B30V31 | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 33200 | 0.54 | 2.42 | 2.44 | 4.66 | 3.947 | 3.98 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 60.9% | 76.02% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10093496 | HRCU-A-CB | 4TWV0036A1 | TAM9A0C36V31 | 35000 | 13.5 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33400 | 32800 | 0.52 | 2.38 | 2.43 | 4.78 | 4.1118 | 3.96 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 60.55% | 76.09% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10093497 | HRCU-A-CB | 4TWV0036A1 | TAM9A0C42V41 | 35600 | 13.5 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33600 | 31200 | 0.51 | 2.2 | 2.53 | 4.82 | 4.4749 | 3.62 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 62.31% | 77.14% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10093500 | HRCU-A-CB | 4TWV0048A1 | TAM9A0C60V51 | 46500 | 12.5 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 12000 | 43000 | 42700 | 0.78 | 2.26 | 3.56 | 4.5 | 5.5747 | 3.52 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 65.9% | 77.95% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093502 | HRCU-A-CB | 4TWV8024A1 | TAM9A0B30V31 | 23800 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20000 | 21000 | 0.54 | 2.6 | 1.55 | 4.34 | 2.2538 | 3.96 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 61.52% | 75.56% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093503 | HRCU-A-CB | 4TWV8024A1 | TAM9A0C36V31 | 24000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 21000 | 21400 | 0.54 | 2.52 | 1.52 | 4.34 | 2.4416 | 4.12 |  | 11320 | 16900 | 16900 | 1.23 | 2.52 | 1.96 | 2.7 | 1.9649 | 2.52 |  | 10830 |  | 12780 | 1.64 |  | 1.9 | 1.94 |  | 1.95 | 59.72% | 75.62% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093504 | HRCU-A-CB | 4TWV8036A1 | TAM9A0B30V31 | 34400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 43900 | 0.53 | 2.4 | 3.45 | 4.64 | 3.9066 | 3.72 |  | 16370 | 26600 | 26800 | 1.84 | 2.4 | 3.27 | 2.6 | 3.2474 | 2.4 |  | 17340 |  | 20760 | 2.6 |  | 3.12 | 1.96 |  | 1.95 | 47.29% | 77.46% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093505 | HRCU-A-CB | 4TWV8036A1 | TAM9A0C36V31 | 35000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32200 | 43400 | 0.52 | 2.36 | 3.36 | 4.68 | 3.9977 | 3.78 |  | 16260 | 26200 | 26400 | 1.85 | 2.36 | 3.27 | 2.58 | 3.2528 | 2.36 |  | 17134 |  | 20500 | 2.64 |  | 3.14 | 1.90 |  | 1.90 | 47.24% | 77.65% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093506 | HRCU-A-CB | 4TWV8036A1 | TAM9A0C42V41 | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30000 | 31200 | 0.51 | 2.22 | 2.54 | 4.82 | 3.9594 | 3.6 |  | 16040 | 25400 | 25700 | 1.91 | 2.22 | 3.39 | 2.46 | 3.3523 | 2.22 |  | 16894 |  | 20040 | 2.72 |  | 3.24 | 1.82 |  | 1.80 | 64.23% | 77.98% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093507 | HRCU-A-CB | 4TWV8037A1 | TAM9A0B30V31 | 35400 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 33200 | 0.54 | 2.42 | 2.44 | 4.66 | 3.947 | 3.98 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 60.9% | 76.02% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093508 | HRCU-A-CB | 4TWV8037A1 | TAM9A0C36V31 | 35000 | 13 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8500 | 32800 | 32200 | 0.52 | 2.38 | 2.3 | 4.78 | 4.0379 | 4.1 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 61.68% | 76.09% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093509 | HRCU-A-CB | 4TWV8037A1 | TAM9A0C42V41 | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30800 | 33300 | 0.51 | 2.2 | 2.68 | 4.82 | 4.102 | 3.64 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 58.38% | 77.14% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093510 | HRCU-A-CB | 4TWV8048A1 | TAM9A0C42V41 | 46500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12300 | 41500 | 42600 | 0.76 | 2.14 | 3.8 | 4.74 | 5.682 | 3.28 |  | 23290 | 36200 | 36600 | 2.81 | 2.14 | 5 | 2.42 | 4.9563 | 2.14 |  | 24456 |  | 28920 | 4.04 |  | 4.8 | 1.78 |  | 1.75 | 67.89% | 79.02% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093511 | HRCU-A-CB | 4TWV8048A1 | TAM9A0C48V41 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41000 | 43000 | 0.76 | 2.36 | 3.46 | 4.58 | 5.0902 | 3.64 |  | 22960 | 36400 | 36800 | 2.59 | 2.36 | 4.57 | 2.6 | 4.5191 | 2.36 |  | 24190 |  | 28780 | 3.68 |  | 4.38 | 1.92 |  | 1.95 | 66.93% | 78.21% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093512 | HRCU-A-CB | 4TWV8048A1 | TAM9A0C60V51 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41500 | 42600 | 0.77 | 2.32 | 3.54 | 4.52 | 5.2411 | 3.52 |  | 22850 | 36200 | 36600 | 2.62 | 2.32 | 4.64 | 2.56 | 4.5718 | 2.32 |  | 24150 |  | 28680 | 3.72 |  | 4.42 | 1.90 |  | 1.90 | 67.32% | 78.36% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093515 | HRCU-A-CB | 4TWV8049A1 | TAM9A0C60V51 | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12000 | 41000 | 31700 | 0.78 | 2.26 | 2.5 | 4.5 | 5.3154 | 3.72 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 88.77% | 77.95% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10093516 | HRCU-A-CB | 4TWV8060A1 | TAM9A0C60V51 | 54000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 18400 | 50500 | 32300 | 1.21 | 2.1 | 2.55 | 4.46 | 7.0459 | 3.72 |  | 33510 | 49500 | 51100 | 3.94 | 2.1 | 7.14 | 2.5 | 6.9064 | 2.1 |  | 34860 |  | 40780 | 5.6 |  | 6.76 | 1.82 |  | 1.75 | 126.3% | 79.8% | N/A |  |  | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10095215 | HRCU-A-CB-O | MUZ-GL09NA-U1 | MSZ-GL09NA-U1 | 9000 | 15.4 | 24.6 | 12.8 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4500 | 10900 | 15900 | 0.23 | 0.72 | 1.25 | 5.734 | 4.4368 | 3.7279 |  | 2830 | 6700 | 10200 | 0.28 | 0.63 | 1.06 | 2.9621 | 3.1168 | 2.8201 |  | 2280 |  | 8000 | 0.24 |  | 0.85 | 2.7842 |  | 2.7583 | 50.31% | 85.71% | MAC-640BH-U | 130 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Wind Free RAC Series | 10103172 | HRCU-A-CB-O | AR09MSWXCWKX | AR09MSWXCWKN | 9000 | 14.05 | 21 | 10 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 11000 | 11330 | 0.16 | 0.86 | 0.903 | 5.4951 | 3.7486 | 3.6772 |  | 3310.9091 | 5500 | 10800 | 0.2586 | 0.62476 | 1.4426 | 3.7522 | 2.58 | 2.1941 |  | 3435.2727 |  | 9680 | 0.29805 |  | 1.6116 | 3.3779 |  | 1.7603 | 85.44% | 89.63% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153439 | HRCU-A-CB | 4A6V0036A1 | TEM8A0C36V31+TDR | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 32700 | 0.51 | 2.44 | 2.37 | 4.72 | 3.8186 | 4.04 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 59.63% | 76.47% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153440 | HRCU-A-CB | 4A6V0036A1 | TEM8A0C42V41+TDR | 35600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 32700 | 0.52 | 2.32 | 2.41 | 4.68 | 3.9656 | 3.98 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 59.33% | 76.38% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153441 | HRCU-A-CB | 4A6V0036A1 | TEM8A0C48V41+TDR | 35600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 31100 | 0.52 | 2.4 | 2.52 | 4.62 | 3.7845 | 3.62 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 63.34% | 76.95% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153442 | HRCU-A-CB | 4A6V0036A1 | TEM8A0D48V41+TDR | 35800 | 13 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 33100 | 0.51 | 2.48 | 2.65 | 4.82 | 3.757 | 3.66 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 60.42% | 76.63% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153444 | HRCU-A-CB | 4A6V0048A1 | TEM8A0C48V41+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 33100 | 0.76 | 2.36 | 2.65 | 4.58 | 5.2144 | 3.66 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 84.53% | 77.72% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 20 | 10153445 | HRCU-A-CB | 4A6V0048A1 | TEM8A0C60V51+TDR | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 32100 | 0.78 | 2.34 | 2.35 | 4.58 | 5.4467 | 4 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 87.54% | 76.78% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153453 | HRCU-A-CB | 4A6V8036A1 | TEM8A0C36V31+TDR | 35200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 42600 | 0.51 | 2.4 | 3.37 | 4.72 | 3.8578 | 3.7 |  | 15930 | 25600 | 25800 | 1.8 | 2.4 | 3.16 | 2.6 | 3.1253 | 2.4 |  | 16728 |  | 20040 | 2.56 |  | 3.02 | 1.92 |  | 1.95 | 47.04% | 77.67% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153454 | HRCU-A-CB | 4A6V8036A1 | TEM8A0C42V41+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 43900 | 0.51 | 2.32 | 3.45 | 4.72 | 3.9908 | 3.72 |  | 15820 | 25600 | 25800 | 1.84 | 2.32 | 3.25 | 2.52 | 3.2331 | 2.32 |  | 16688 |  | 19940 | 2.62 |  | 3.12 | 1.86 |  | 1.85 | 45.42% | 77.29% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153455 | HRCU-A-CB | 4A6V8036A1 | TEM8A0C48V41+TDR | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 31000 | 43600 | 0.52 | 2.42 | 3.38 | 4.5 | 3.7533 | 3.78 |  | 15820 | 25400 | 25700 | 1.78 | 2.42 | 3.11 | 2.6 | 3.0753 | 2.42 |  | 16788 |  | 20040 | 2.52 |  | 3 | 1.96 |  | 1.95 | 45.96% | 77.98% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153456 | HRCU-A-CB | 4A6V8036A1 | TEM8A0D48V41+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31600 | 43200 | 0.51 | 2.46 | 3.43 | 4.76 | 3.7637 | 3.7 |  | 15930 | 25800 | 26100 | 1.78 | 2.46 | 3.11 | 2.62 | 3.0729 | 2.46 |  | 16788 |  | 20100 | 2.52 |  | 3 | 1.96 |  | 1.95 | 46.53% | 77.01% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153458 | HRCU-A-CB | 4A6V8037A1 | TEM8A0C36V31+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 31200 | 0.51 | 2.44 | 2.38 | 4.72 | 3.8186 | 3.84 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 62.5% | 76.47% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153459 | HRCU-A-CB | 4A6V8037A1 | TEM8A0C42V41+TDR | 35600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 31300 | 0.52 | 2.32 | 2.35 | 4.68 | 3.9656 | 3.9 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 61.98% | 76.38% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153460 | HRCU-A-CB | 4A6V8037A1 | TEM8A0C48V41+TDR | 35600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 32300 | 0.52 | 2.4 | 2.31 | 4.62 | 3.7845 | 4.1 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 4.38 | 1.90 |  | 1.95 | 60.99% | 76.95% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153461 | HRCU-A-CB | 4A6V8037A1 | TEM8A0D48V41+TDR | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 31700 | 0.51 | 2.48 | 2.49 | 4.82 | 3.757 | 3.74 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 4.38 | 1.94 |  | 1.95 | 63.09% | 76.63% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153463 | HRCU-A-CB | 4A6V8048A1 | TEM8A0C48V41+TDR | 46500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42500 | 43400 | 0.81 | 2.24 | 3.5 | 4.3 | 5.5591 | 3.64 |  | 21310 | 34200 | 35100 | 2.62 | 2.24 | 4.61 | 2.38 | 4.4734 | 2.24 |  | 21900 |  | 26460 | 3.68 |  | 4.38 | 1.74 |  | 1.75 | 60.97% | 75.38% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153464 | HRCU-A-CB | 4A6V8048A1 | TEM8A0C60V51+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12100 | 44500 | 44000 | 0.78 | 2.4 | 3.47 | 4.54 | 5.4327 | 3.72 |  | 22630 | 36800 | 37200 | 2.58 | 2.4 | 4.56 | 2.56 | 4.4926 | 2.4 |  | 23744 |  | 28520 | 3.64 |  | 4.38 | 1.92 |  | 1.90 | 64.82% | 76.67% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153468 | HRCU-A-CB | 4A6V8049A1 | TEM8A0C48V41+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 32700 | 0.76 | 2.36 | 2.42 | 4.58 | 5.2144 | 3.96 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.38 | 1.90 |  | 1.90 | 85.57% | 77.72% | N/A |  |  | N/A
American Standard | American Standard | AccuComfort Platinum 18 | 10153469 | HRCU-A-CB | 4A6V8049A1 | TEM8A0C60V51+TDR | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 31000 | 0.78 | 2.34 | 2.5 | 4.58 | 5.4467 | 3.64 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 90.65% | 76.78% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153696 | HRCU-A-CB | 4TWV0036A1 | TEM8A0C36V31+TDR | 35400 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 32700 | 0.51 | 2.44 | 2.37 | 4.72 | 3.8186 | 4.04 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 59.63% | 76.47% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153698 | HRCU-A-CB | 4TWV0036A1 | TEM8A0C42V41+TDR | 35600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 32700 | 0.52 | 2.32 | 2.41 | 4.68 | 3.9656 | 3.98 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 59.33% | 76.38% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153699 | HRCU-A-CB | 4TWV0036A1 | TEM8A0C48V41+TDR | 35600 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 31100 | 0.52 | 2.4 | 2.52 | 4.62 | 3.7845 | 3.62 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 63.34% | 76.95% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153700 | HRCU-A-CB | 4TWV0036A1 | TEM8A0D48V41+TDR | 35800 | 13 | 19.5 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 33100 | 0.51 | 2.48 | 2.65 | 4.82 | 3.757 | 3.66 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 60.42% | 76.63% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153703 | HRCU-A-CB | 4TWV0048A1 | TEM8A0C48V41+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 33100 | 0.76 | 2.36 | 2.65 | 4.58 | 5.2144 | 3.66 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 84.53% | 77.72% | N/A |  |  | N/A
Trane | Trane | TruComfort XV20i | 10153704 | HRCU-A-CB | 4TWV0048A1 | TEM8A0C60V51+TDR | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 32100 | 0.78 | 2.34 | 2.35 | 4.58 | 5.4467 | 4 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 87.54% | 76.78% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153714 | HRCU-A-CB | 4TWV8036A1 | TEM8A0C36V31+TDR | 35200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 42600 | 0.51 | 2.4 | 3.37 | 4.72 | 3.8578 | 3.7 |  | 15930 | 25600 | 25800 | 1.8 | 2.4 | 3.16 | 2.6 | 3.1253 | 2.4 |  | 16728 |  | 20040 | 2.56 |  | 3.02 | 1.92 |  | 1.95 | 47.04% | 77.67% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153716 | HRCU-A-CB | 4TWV8036A1 | TEM8A0C42V41+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 43900 | 0.51 | 2.32 | 3.45 | 4.72 | 3.9908 | 3.72 |  | 15820 | 25600 | 25800 | 1.84 | 2.32 | 3.25 | 2.52 | 3.2331 | 2.32 |  | 16688 |  | 19940 | 2.62 |  | 3.12 | 1.86 |  | 1.85 | 45.42% | 77.29% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153717 | HRCU-A-CB | 4TWV8036A1 | TEM8A0C48V41+TDR | 36200 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8000 | 31000 | 43600 | 0.52 | 2.42 | 3.38 | 4.5 | 3.7533 | 3.78 |  | 15820 | 25400 | 25700 | 1.78 | 2.42 | 3.11 | 2.6 | 3.0753 | 2.42 |  | 16788 |  | 20040 | 2.52 |  | 3 | 1.96 |  | 1.95 | 45.96% | 77.98% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153718 | HRCU-A-CB | 4TWV8036A1 | TEM8A0D48V41+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31600 | 43200 | 0.51 | 2.46 | 3.43 | 4.76 | 3.7637 | 3.7 |  | 15930 | 25800 | 26100 | 1.78 | 2.46 | 3.11 | 2.62 | 3.0729 | 2.46 |  | 16788 |  | 20100 | 2.52 |  | 3 | 1.96 |  | 1.95 | 46.53% | 77.01% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153721 | HRCU-A-CB | 4TWV8037A1 | TEM8A0C36V31+TDR | 35400 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 31200 | 0.51 | 2.44 | 2.38 | 4.72 | 3.8186 | 3.84 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 62.5% | 76.47% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153722 | HRCU-A-CB | 4TWV8037A1 | TEM8A0C42V41+TDR | 35600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 31300 | 0.52 | 2.32 | 2.35 | 4.68 | 3.9656 | 3.9 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 61.98% | 76.38% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153724 | HRCU-A-CB | 4TWV8037A1 | TEM8A0C48V41+TDR | 35600 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 32300 | 0.52 | 2.4 | 2.31 | 4.62 | 3.7845 | 4.1 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 60.99% | 76.95% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153725 | HRCU-A-CB | 4TWV8037A1 | TEM8A0D48V41+TDR | 35800 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 31700 | 0.51 | 2.48 | 2.49 | 4.82 | 3.757 | 3.74 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 63.09% | 76.63% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153728 | HRCU-A-CB | 4TWV8048A1 | TEM8A0C48V41+TDR | 46500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42500 | 43400 | 0.81 | 2.24 | 3.5 | 4.3 | 5.5591 | 3.64 |  | 21310 | 34200 | 35100 | 2.62 | 2.24 | 4.61 | 2.38 | 4.4734 | 2.24 |  | 21900 |  | 26460 | 3.68 |  | 4.4 | 1.74 |  | 1.75 | 60.97% | 75.38% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153729 | HRCU-A-CB | 4TWV8048A1 | TEM8A0C60V51+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12100 | 44500 | 44000 | 0.78 | 2.4 | 3.47 | 4.54 | 5.4327 | 3.72 |  | 22630 | 36800 | 37200 | 2.58 | 2.4 | 4.56 | 2.56 | 4.4926 | 2.4 |  | 23744 |  | 28520 | 3.64 |  | 4.36 | 1.92 |  | 1.90 | 64.82% | 76.67% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153734 | HRCU-A-CB | 4TWV8049A1 | TEM8A0C48V41+TDR | 47500 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 32700 | 0.76 | 2.36 | 2.42 | 4.58 | 5.2144 | 3.96 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 85.57% | 77.72% | N/A |  |  | N/A
Trane | Trane | TruComfort XV18 | 10153735 | HRCU-A-CB | 4TWV8049A1 | TEM8A0C60V51+TDR | 47000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 31000 | 0.78 | 2.34 | 2.5 | 4.58 | 5.4467 | 3.64 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 90.65% | 76.78% | N/A |  |  | N/A
Panasonic | Panasonic | RAC Multi E | 10221199 | HMSV-A-CB | CU-3E19RBU-5 | Non-Ducted Indoor Unit | 19000 | 12.55 | 22 | 10.5 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5500 | 26000 | 28400 | 0.32 | 2.06 | 2.3 | 5 | 3.7 | 3.61 |  | 4100 | 19800 | 20800 | 0.37 | 2.37 | 2.85 | 3.2496 | 2.45 | 2.1402 |  | 3800 |  | 18900 | 0.37 |  | 2.64 | 3.01 |  | 2.1 | 66.55% | 90.87% | Accessory for outdoor unit CU-3E19RBU-5; Wind Baffle # WINDB-M1 |  |  | -5°F | 2000 |  | 10500 | 0.26 | 1.85 | 2.26 | 1.66
Nortek Global | Maytag | M1200 | 10296728 | HRCU-A-CB | PSH1BG4CVRX24K | B6VMAX24K-B | 24600 | 13.9 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 10200 | 22400 | 24700 | 0.7 | 1.7 | 2.2 | 4.2705 | 3.8616 | 3.2904 |  | 6100 | 14200 | 15800 | 0.7 | 1.5 | 1.9 | 2.5539 | 2.7744 | 2.4371 |  | 4700 |  | 12600 | 0.6 |  | 1.8 | 2.2957 |  | 2.0515 | 51.01% | 79.75% | N/A |  |  | N/A
Nortek Global | Maytag | M1200 | 10296733 | HRCU-A-CB | PSH1BG4CVRX36K | B6VMAX36K-B | 34800 | 12.6 | 19 | 10 | Yes | Centrally Ducted | N/A | N/A | 16500 | 34400 | 36800 | 1 | 2.7 | 3.2 | 4.8357 | 3.7339 | 3.3703 |  | 9900 | 21800 | 23900 | 1 | 2.4 | 2.7 | 2.9014 | 2.6621 | 2.5942 |  | 7500 |  | 20100 | 0.9 |  | 2.6 | 2.4423 |  | 2.2657 | 54.62% | 84.1% | N/A |  |  | N/A
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10298668 | HMSV-A-CB | AJ030MCS4CH/AA | Non-ducted | 28400 | 12.5 | 18 | 11 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 28600 | 28600 | 0.45 | 2.09 | 2.09 | 4.9496 | 4.0104 | 4.0104 |  | 13100 | 18500 | 28600 | 1.65 | 1.95 | 4 | 2.3268 | 2.7804 | 2.0955 |  | 13100 |  | 28600 | 1.9 |  | 4.65 | 2.0206 |  | 1.8025 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 2 | 3.8 | 1.4654 | 1.5425
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10298670 | HMSV-A-CB | AJ024MCS4CH/AA | Non-ducted | 25000 | 12.5 | 19 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 25000 | 25000 | 0.45 | 1.83 | 1.83 | 4.9496 | 4.0037 | 4.0037 |  | 13000 | 14000 | 25000 | 1.5 | 1.55 | 3.45 | 2.5399 | 2.6471 | 2.1237 |  | 12000 |  | 25000 | 1.7 |  | 4 | 2.0687 |  | 1.8317 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 1.95 | 3.9 | 1.5029 | 1.5029
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298956 | HRCU-A-CB-O | HP-25EACH09R2O | HP-25EACH09R2I | 9000 | 14.5 | 25 | 11.2 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | Temp. below 0 degrees | N/A
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298957 | HRCU-A-CB-O | HP-22EACH12R2O | HP-22EACH12R2I | 12000 | 13 | 22.5 | 12 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.3 | 3.54 | 3.27 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.64 | 2.64 | 2.21 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | Temp. below 0 degrees | N/A
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298959 | HRCU-A-CB-O | HP-20EACH24R2O | HP-20EACH24R2I | 24000 | 13 | 20.5 | 11.5 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.03 | 3.6 | 2.72 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.76 | 2.76 | 1.95 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.78 |  | 1.81 | 82.85% | 95.64% | Integrated | 150 | Temp. below 0 degrees | N/A
Daikin AC (Americas), Inc | Daikin | Vista | 10318063 | HRCU-A-CB-O | RX18QMVJU | FFQ18Q2VJU | 17400 | 12.5 | 19.3 | 10.1 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 5400 | 21600 | 21800 | 0.37 | 1.88 | 1.92 | 4.2773 | 3.3672 | 3.3276 |  | 3640 | 12490 | 12610 | 0.33 | 1.33 | 1.36 | 3.24 | 2.74 | 2.72 |  | 2800 |  | 9700 | 0.31 |  | 1.27 | 2.6471 |  | 2.2384 | 44.5% | 76.92% | accessory (KEH063A4E) | 140 | Temp below 23 degrees | N/A
Amana Heating and air Conditioning | Amana | AVZC20 | 10324704 | HRCU-A-CB | AVZC200241A* | CA*F3642*6D*+MBVC1200**-1A*+TX | 23400 | 13 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 5507 | 23600 | 23600 | 0.328 | 1.87 | 1.87 | 4.9206 | 3.6987 | 3.6987 |  | 3943 | 13915 | 15200 | 0.338 | 1.487 | 1.82 | 3.4189 | 2.7425 | 2.4476 |  | 1650 |  | 11400 | 0.296 |  | 1.6 | 1.63 |  | 2.09 | 48.31% | 75% | N/A |  |  | N/A
Amana Heating and air Conditioning | Amana | AVZC20 | 10324705 | HRCU-A-CB | AVZC200361A* | CA*F3743*6D*+MBVC1600**-1A*+TX | 35400 | 14 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 13438 | 35000 | 35000 | 0.721 | 2.48 | 2.48 | 5.46 | 4.14 | 4.14 |  | 8580 | 18365 | 28800 | 0.722 | 2.092 | 3.72 | 3.48 | 2.57 | 2.27 |  | 5135 |  | 22100 | 0.722 |  | 3.48 | 2.08 |  | 1.86 | 63.14% | 76.74% | N/A |  |  | N/A
Amana Heating and air Conditioning | Amana | AVZC20 | 10324706 | HRCU-A-CB | AVZC200481A* | CA*F4961*6D*+MBVC2000**-1A*+TX | 46500 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 13274 | 45500 | 45500 | 0.796 | 3.42 | 3.42 | 4.8872 | 3.899 | 3.899 |  | 8394 | 28254 | 34000 | 0.766 | 2.926 | 4.15 | 3.21 | 2.83 | 2.4 |  | 5390 |  | 26000 | 0.722 |  | 3.87 | 2.19 |  | 1.97 | 57.14% | 76.47% | N/A |  |  | N/A
Amana Heating and air Conditioning | Amana | AVZC20 | 10324707 | HRCU-A-CB | AVZC200601A* | CA*F4961*6D*+MBVC2000**-1A*+TX | 52500 | 12.5 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 15848 | 50000 | 50000 | 0.891 | 3.76 | 3.76 | 5.2128 | 3.8972 | 3.8972 |  | 9302 | 32293 | 34000 | 0.92 | 3.466 | 4.07 | 2.96 | 2.73 | 2.45 |  | 5407 |  | 26000 | 0.901 |  | 3.85 | 1.76 |  | 1.98 | 52% | 76.47% | N/A |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324709 | HRCU-A-CB | DZ20VC0241B | CA*F3642*6D*+MBVC1200**-1A*+TXV | 23400 | 13 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 5507 | 23600 | 23600 | 0.33 | 1.87 | 1.87 | 4.91 | 3.7 | 3.7 |  | 3943 | 13915 | 15200 | 0.338 | 1.487 | 1.82 | 3.419 | 2.74 | 2.45 |  | 1650 |  | 11400 | 0.296 |  | 1.6 | 1.63 |  | 2.09 | 48.31% | 75% | N/A |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324711 | HRCU-A-CB | DZ20VC0361B | CA*F3743*6D*+MBVC1600**-1A*+TXV | 35400 | 14 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 13438 | 35000 | 35000 | 0.721 | 2.48 | 2.48 | 5.46 | 4.14 | 4.14 |  | 8580 | 18365 | 28800 | 0.722 | 2.092 | 3.72 | 3.4829 | 2.57 | 2.27 |  | 5135 |  | 22100 | 0.722 |  | 3.48 | 2.08 |  | 1.86 | 63.14% | 76.74% | N/A |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324713 | HRCU-A-CB | DZ20VC0481B | CA*F4961*6D*+MBVC2000**-1A*+TXV | 46500 | 13 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 13274 | 45500 | 45500 | 0.796 | 3.42 | 3.42 | 4.88 | 3.9 | 3.9 |  | 8394 | 28254 | 34000 | 0.766 | 2.926 | 4.15 | 3.2117 | 2.83 | 2.4 |  | 5390 |  | 26000 | 0.722 |  | 3.87 | 2.19 |  | 1.97 | 57.14% | 76.47% | N/A |  |  | N/A
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324715 | HRCU-A-CB | DZ20VC0601B | CA*F4961*6D*+MBVC2000**-1A*+TXV | 52500 | 12.5 | 20 | 10 | Yes | Centrally Ducted | N/A | N/A | 15848 | 50000 | 50000 | 0.891 | 3.76 | 3.76 | 5.21 | 3.9 | 3.9 |  | 9302 | 32293 | 34000 | 0.92 | 3.466 | 4.07 | 2.96 | 2.73 | 2.45 |  | 5407 |  | 26000 | 0.901 |  | 3.85 | 1.76 |  | 1.98 | 52% | 76.47% | N/A |  |  | N/A
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10348192 | HMSV-A-CB | AJ020MCS3CH/AA | Non-ducted | 21000 | 12.5 | 18 | 10 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 22000 | 22000 | 0.45 | 1.61 | 1.61 | 4.9496 | 4.0047 | 4.0047 |  | 13000 | 13000 | 22000 | 1.6 | 1.45 | 2.9 | 2.3812 | 2.6275 | 2.2233 |  | 12000 |  | 22000 | 1.8 |  | 3.3 | 1.9538 |  | 1.9538 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 1.95 | 4 | 1.5029 | 1.4654
LG Electronics USA, Inc. | LG |  | 10399150 | HRCU-A-CB-O | LUU368HV | LVN360HV4 | 36000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 15000 | 40000 | 47000 | 1.35 | 3.39 | 5.5 | 3.2563 | 3.4581 | 2.5044 |  | 8900 | 25600 | 32000 | 1.22 | 2.75 | 4.5 | 2.138 | 2.7282 | 2.0841 |  | 7000 |  | 30000 | 1.11 |  | 4.4 | 1.8482 |  | 1.9982 | 63.83% | 93.75% |  |  |  | -4 |  |  | 17310 |  | 3.32 |  | 1.4593
LG Electronics USA, Inc. | LG |  | 10443471 | HMSV-A-CB | LMU420HHV | NON- DUCTED INDOOR UNITS | 42000 | 14 | 20.5 | 11 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 45000 | 55260 | 0.96 | 3.3 | 4.48 | 4.1076 | 3.9964 | 3.615 |  | 9466 | 29000 | 49950 | 0.91 | 3.04 | 5.62 | 3.0486 | 3.0487 | 2.6048 |  | 7688 |  | 45000 | 0.87 |  | 6.14 | 2.5898 |  | 2.1479 | 81.43% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10443472 | HMSV-A-CB | LMU360HHV | NON- DUCTED INDOOR UNITS | 36000 | 15 | 21 | 11.5 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 41000 | 50200 | 0.96 | 2.93 | 3.94 | 4.1076 | 4.101 | 3.7341 |  | 9466 | 28000 | 45510 | 0.91 | 2.83 | 5.2 | 3.0486 | 3.0487 | 2.5649 |  | 7688 |  | 41000 | 0.87 |  | 5.69 | 2.5898 |  | 2.1118 | 81.67% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10443472 | HMSV-A-CB | LMU360HHV | NON- DUCTED INDOOR UNITS | 36000 | 15 | 21 | 11.5 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 41000 | 50200 | 0.96 | 2.93 | 3.94 | 4.1076 | 4.101 | 3.7341 |  | 9466 | 28000 | 45510 | 0.91 | 2.83 | 5.2 | 3.0486 | 3.0487 | 2.5649 |  | 7688 |  | 41000 | 0.87 |  | 5.69 | 2.5898 |  | 2.1118 | 81.67% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10443474 | HMSV-A-CB | LMU420HHV | DUCTED INDOOR UNITS | 42000 | 13 | 19 | 10.5 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 13455 | 45000 | 54900 | 1.07 | 3.66 | 4.81 | 3.6853 | 3.6033 | 3.345 |  | 9466 | 29000 | 49950 | 1.02 | 3.14 | 5.84 | 2.7198 | 2.7199 | 2.5067 |  | 7688 |  | 45000 | 0.98 |  | 6.38 | 2.2991 |  | 2.0671 | 81.97% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10443475 | HMSV-A-CB | LMU360HHV | DUCTED INDOOR UNITS | 34000 | 13.5 | 17.5 | 10.5 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 13127 | 40000 | 49200 | 1.17 | 3.55 | 4.48 | 3.2882 | 3.3022 | 3.2185 |  | 9239 | 27000 | 44400 | 1.11 | 3.16 | 5.32 | 2.4394 | 2.4395 | 2.4459 |  | 7483 |  | 40000 | 1.07 |  | 5.84 | 2.0496 |  | 2.0073 | 81.3% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10444103 | HMSV-A-CB | LMU420HHV | MIXED DUCTED AND DUCTLESS | 42000 | 13.5 | 19.75 | 10.75 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 13445 | 45000 | 55080 | 1.02 | 3.47 | 4.65 | 3.8631 | 3.8006 | 3.4715 |  | 9466 | 29000 | 49950 | 1.01 | 3.09 | 5.73 | 2.7467 | 2.7469 | 2.5548 |  | 7688 |  | 45000 | 0.93 |  | 6.26 | 2.4227 |  | 2.1067 | 81.7% | 90.09% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10445372 | HMSV-A-CB | LMU180HHV | NON- DUCTED INDOOR UNITS | 18000 | 13.5 | 21 | 10 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 22000 | 24000 | 1.25 | 2.22 | 3.11 | 2.4027 | 2.9043 | 2.2616 |  | 7511 | 14700 | 23600 | 1.02 | 1.72 | 3.31 | 2.1581 | 2.1582 | 2.0896 |  | 6262 |  | 22000 | 0.91 |  | 3.48 | 2.0167 |  | 1.8527 | 91.67% | 93.22% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10445374 | HMSV-A-CB | LMU240HHV | NON- DUCTED INDOOR UNITS | 24000 | 13.5 | 21 | 10.7 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 26000 | 31200 | 1.26 | 2.12 | 2.96 | 2.3836 | 3.5943 | 3.0891 |  | 7511 | 17400 | 28500 | 1.04 | 1.82 | 3.45 | 2.1166 | 2.1167 | 2.421 |  | 6262 |  | 26000 | 0.94 |  | 3.63 | 1.9524 |  | 2.0991 | 83.33% | 91.23% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10445376 | HMSV-A-CB | LMU300HHV | NON- DUCTED INDOOR UNITS | 28400 | 12.5 | 20 | 11 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 28600 | 34200 | 1.3 | 2.33 | 3.26 | 2.3103 | 3.5974 | 3.0745 |  | 7511 | 18900 | 31600 | 1.08 | 1.98 | 3.69 | 2.0382 | 2.0383 | 2.5098 |  | 6262 |  | 28600 | 0.97 |  | 3.88 | 1.892 |  | 2.1603 | 83.63% | 90.51% | Integrated | 120 | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0
LG Electronics USA, Inc. | LG |  | 10513887 | HRCU-A-CB-O | LUU248HV | LVN240HV4 | 24000 | 12.5 | 18 | 10 | Yes | Centrally Ducted | N/A | N/A | 10000 | 27000 | 30000 | 0.75 | 2.26 | 2.8 | 3.9076 | 3.5013 | 3.14 |  | 6000 | 18000 | 22000 | 0.72 | 1.9 | 3 | 2.4423 | 2.7765 | 2.1492 |  | 4800 |  | 20000 | 0.69 |  | 3.2 | 2.0388 |  | 1.8317 | 66.67% | 90.91% |  |  |  | -4 |  |  | 21660 |  | 4.35 |  | 1.528
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10595346 | HRCU-A-CB | DZ20VC0241B* | CHPF3642C6C*+MBVC1200**-1A*+TXV | 23400 | 13 | 21 | 10 | Yes | Centrally Ducted | N/A | N/A | 5188 | 23400 | 23959 | 0.324 | 2.063 | 1.995 | 4.6928 | 3.3242 | 3.5196 |  | 1420 | 13000 | 14990 | 0.336 | 1.465 | 1.71 | 1.2386 | 2.6006 | 2.5691 |  | 958 |  | 11648 | 0.377 |  | 1.597 | 0.74473 |  | 2.1376 | 48.62% | 77.71% | N/A |  |  | N/A | [7 empty] | 2018-01-18
Carrier | Carrier | Infinity | 201753408 | HRCU-A-CB-O | 38MPRAQ09AA3 | 40MPHAQ09XA3 | 9000 | 15 | 42 | 15 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 2750 | 10000 | 17012 | 0.159 | 0.7325 | 1.691 | 5.0688 | 4.001 | 2.9484 |  | 2200 | 7200 | 15488 | 0.191 | 0.7589 | 2.155 | 3.3757 | 2.7805 | 2.1063 |  | 1925 |  | 13047 | 0.172 |  | 1.936 | 3.28 |  | 1.9751 | 76.69% | 84.24% | integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Bryant | Bryant | Evolution | 201753409 | HRCU-A-CB-O | 38MPRAQ09AA3 | 619PHAQ09XA3 | 9000 | 15 | 42 | 15 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 2750 | 10000 | 17012 | 0.159 | 0.7325 | 1.691 | 5.0688 | 4.001 | 2.9484 |  | 2200 | 7200 | 15488 | 0.191 | 0.7589 | 2.155 | 3.3757 | 2.7805 | 2.1063 |  | 1925 |  | 13047 | 0.172 |  | 1.936 | 3.28 |  | 1.9751 | 76.69% | 84.24% | integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Payne | Payne |  | 201753410 | HRCU-A-CB-O | 38MPRAQ09AA3 | DHMPHAQ09XA3 | 9000 | 15 | 42 | 15 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 2750 | 10000 | 17012 | 0.159 | 0.7325 | 1.691 | 5.0688 | 4.001 | 2.9484 |  | 2200 | 7200 | 15488 | 0.191 | 0.7589 | 2.155 | 3.3757 | 2.7805 | 2.1063 |  | 1925 |  | 13047 | 0.172 |  | 1.936 | 3.28 |  | 1.9751 | 76.69% | 84.24% | integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Carrier | Carrier | Infinity | 201753411 | HRCU-A-CB-O | 38MPRAQ12AA3 | 40MPHAQ12XA3 | 12000 | 13.5 | 32 | 14 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 19100 | 0.188 | 0.829 | 1.973 | 5.7055 | 4.2423 | 2.8371 |  | 2928 | 6800 | 16596 | 0.226 | 0.754 | 2.217 | 3.797 | 2.6431 | 2.1939 |  | 2562 |  | 12897 | 0.203 |  | 2.074 | 3.6988 |  | 1.8224 | 67.52% | 77.71% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Bryant | Bryant | Evolution | 201753412 | HRCU-A-CB-O | 38MPRAQ12AA3 | 619PHAQ12XA3 | 12000 | 13.5 | 32 | 14 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 19100 | 0.188 | 0.829 | 1.973 | 5.7055 | 4.2423 | 2.8371 |  | 2928 | 6800 | 16596 | 0.226 | 0.754 | 2.217 | 3.797 | 2.6431 | 2.1939 |  | 2562 |  | 12897 | 0.203 |  | 2.074 | 3.6988 |  | 1.8224 | 67.52% | 77.71% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Payne | Payne |  | 201753413 | HRCU-A-CB-O | 38MPRAQ12AA3 | DHMPHAQ12XA3 | 12000 | 13.5 | 32 | 14 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 19100 | 0.188 | 0.829 | 1.973 | 5.7055 | 4.2423 | 2.8371 |  | 2928 | 6800 | 16596 | 0.226 | 0.754 | 2.217 | 3.797 | 2.6431 | 2.1939 |  | 2562 |  | 12897 | 0.203 |  | 2.074 | 3.6988 |  | 1.8224 | 67.52% | 77.71% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2018-03-05
Midea | Midea |  | 201753970 | HRCU-A-CB-O | 38MPRAQ09AA3 | DHMPHAQ09XA3 | 9000 | 15 | 42 | 15 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 2750 | 10000 | 17012 | 0.159 | 0.7325 | 1.691 | 5.0688 | 4.001 | 2.9484 |  | 2200 | 7200 | 15488 | 0.191 | 0.7589 | 2.155 | 3.3757 | 2.7805 | 2.1063 |  | 1925 |  | 13047 | 0.172 |  | 1.936 | 3.28 |  | 1.9751 | 76.69% | 84.24% | integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  |  | 0 |  |  |  |  | 2018-03-05
Midea | Midea |  | 201753971 | HRCU-A-CB-O | 38MPRAQ12AA3 | DHMPHAQ12XA3 | 12000 | 13.5 | 32 | 14 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 19100 | 0.188 | 0.829 | 1.973 | 5.7055 | 4.2423 | 2.8371 |  | 2928 | 6800 | 16596 | 0.226 | 0.754 | 2.217 | 3.797 | 2.6431 | 2.1939 |  | 2562 |  | 12897 | 0.203 |  | 2.074 | 3.6988 |  | 1.8224 | 67.52% | 77.71% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  |  | 0 |  |  |  |  | 2018-03-05

## Sheet1 (hidden)
Manufacturer | Brand (if applicable) | Model Name | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ductless or Centrally Ducted | If Ductless, Multi-zone or Single-zone? | Ductless Indoor Type | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F | COP at Max. Capacity 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F | COP at Max. Capacity X°F | 15 max cap- 5 max cap
American Standard | American Standard |  | 9150124 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Mini-Splits | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 | 2600 | 13304 | 0.22 | 1.79 | 3.4636 | 2.1782 | 0.71144 | 1.4782 | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | -4304
Bryant | Bryant | Evolution Series | 9893607 | 280ANV036000 | FE4ANF002L | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.6094 | 11310.2 | 33496 | 2.1432 | 3.5796 | 1.5466 | 2.7424 | 0.94621 | 1.0946 | N/A |  |  | N/A | [7 empty] | -2896
Carrier | Carrier |  | 9892658 | 25VNA036A030 | FE4ANF002L | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.3838 | 11310.2 | 33496 | 2.1432 | 3.5796 | 1.5466 | 2.7424 | 0.94621 | 1.0946 | N/A |  |  | N/A | [7 empty] | -2896
Carrier | Bryant | Preferred Series | 9854627 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-Ducted Indoor Units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 0.7584 | 1.0199 | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | -550
Carrier | Carrier |  | 9854626 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-Ducted Indoor Units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 0.7584 | 1.0199 | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | -550
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038628 | WSM18MH20S/O | WSM18MH20S/I | HRCU-A-CB-O | 10 | 22 | 13 | 18000 | Yes | Ductless | Single-zone | Mini-Splits | 6093 | 18000 | 19146 | 0.37915 | 1.6695 | 1.5896 | 4.7097 | 3.1599 | 3.5299 | 11100 | 11100 | 12396 | 1.1787 | 1.1787 | 1.5013 | 2.7599 | 2.7599 | 2.4199 | 10460.09 | 12500 | 1.5252 | 2.0816 | 2.0099 | 1.7599 | 0.65288 | 1.0084 | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | -104
Trane | Trane |  | 9150123 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Mini-Splits | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 | 2600 | 13304 | 0.22 | 1.789 | 3.4636 | 2.1794 | 0.71144 | 1.4782 | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | -4304

## Delisted (on 1.1.17)
Manufacturer | Brand (if applicable) | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | HSPF (Region IV): | SEER | EER (@ 95°F) | ENERGY STAR Certified | Ductless or Ducted | If Ductless, Multi-zone or Single-zone? | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Minimum Input Power 47°F | Rated Input Power 47°F | Maximum Input Power 47°F | Minimum COP 47°F | Rated COP 47°F | Maximum COP 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Minimum Input Power 17°F | Rated Input Power 17°F | Maximum Input Power 17°F | Minimum COP 17°F | Rated COP 17°F | Maximum COP 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Minimum Input Power 5°F | Maximum Input Power 5°F | Minimum COP 5°F | Maximum COP 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Minimum Input Power X°F | Maximum Input Power X°F | Minimum COP X°F | Maximum COP X°F
LG |  | 7180060 | LMU18CHV | Non-Ducted Indoor Units | 9.7 | 22 | 13 | Yes | Ductless | Multi-zone | 10248 | 22000 | 24000 | 1.155 | 2.04 | 2.42 | 2.6 | 3.2 | 2.9 | 6288 | 13500 | 19161 | 0.924 | 1.63 | 2.03 | 2 | 2.4 | 2.8 | 4950 | 14807 | 0.861 | 1.86 | 1.7 | 2.3 | 61.7% | 77.28% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Carrier | Bryant | 9854623 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 9854622 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Lennox Industries, Inc. | Lennox | 8994419 | MLA018S4M-1P | non-ducted indoor units | 9.8 | 21.5 | 12.5 | Yes | Ductless | Multizone | 6020 | 20000 | 28500 | 0.715 | 1.72 | 2.7 | 2.4675 | 3.4078 | 3.0935 | 5743 | 12600 | 26457 | 0.804 | 1.388 | 3.978 | 2.0934 | 2.6604 | 1.9492 | 5516 | 24120 | 0.832 | 3.892 | 1.943 | 1.8163 | 84.63% | 91.17% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Mitsubishi |  | 7451974 | MXZ-2C20NAHZ | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98
Mitsubishi |  | 8996530 | MXZ-2C20NAHZ2 | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98

## Sheet2
Manufacturer | Brand (if applicable) | Model | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ducted or Ductless | If Ductless, "Multizone or Singlezone" | Ductless Indoor type | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  | Input Power (kW) |  | COP |  | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Capacity (btu/hr) |  | Input Power (kW) |  | COP
[15 empty] | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum |  |  |  |  | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum
Carrier | Carrier;Bryant |  | 10056166 | 38MAQB18R--3 | 40MBCQ18---3 | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 16000 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.4 | 2.55 | 2.06 | 2660 | 19010 | 0.23 | 3.18 | 3.39 | 1.75 | Integrated | 3 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | 0 | 0 | 0 | 0 | 0 | 0 | 0