## C&I Lighting
C&I Lighting
Logger Level
Data Field | Description | Notes
Logger ID | SerialM | Unique ID for logger. Serial = logger serial number; M = first character of logger make name (e.g., D for Dent, H for HOBO). If a piece of equipment does not have a logger number, a unique identifier can be established by the provider.
Logger Raw Data ID | SerialM_mmddyy | (If applicable) Unique ID for raw logger file. SerialM = Logger ID (above field); mmdd = logger retrieval day, month, and year.
Extrapolated Logger Data ID | Arbitrary* | (If applicable) *File name can be arbitrary but needs to have unique Logger ID (i.e., SerialM) to identify the logger used to generate the extrapolated data
Logger Make | DENT, HOBO, MSR, etc.
Logger Model |  | If applicable
Logger Serial Number (if applicable) |  | Serial Number given by manufacturer. Some measurement tools will not have a serial number. An arbitrary identifier will be used in these situations (e.g., hand held lumen level meters)
Last Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format). For field calibrated loggers, calibration date/time is installation date/time
NIST Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Logging Method | Event, Interval, Instantaneous | Indicates data point type, where Event is a state or TOU meter with no predetermined logging interval, and Interval is a meter with a predetermined logging/sampling interval. The Instantaneous method is for devices taking a single measurement (Drop Down List)
Logging Data Unit | kW, kWh, %, Boolean (0/1; on/off) | The raw data point's unit or metric (e.g., power meters record date/time and connected kW every 5 min, event lighting loggers record date/time and on/off state every time there is state change, interval lighting loggers record date/time and % on during that interval, etc.)
Logging Interval (if applicable) |  | Time format (h:mm:ss)
Date Installed |  | mm/dd/yyyy
Date/Time Logging Started |  | mm/dd/yyyy hhmm (24 hour format)
Date/Time Logging Ended |  | mm/dd/yyyy hhmm (24 hour format)
Date Removed |  | mm/dd/yyyy
Install Location (Room Type) | Office, Bathroom, Hall, Mech. Room, Sales Floor, Plant floor, etc. | Description of logger location (Drop down list)
Logger kW (if applicable) | kW of fixture in which logger installed | kW of fixture being specifically logged - the fixture that the logger's sensor reacts to.
Fixture Control | Switch, Dimmer, occupancy sensors, day lighting control, Bi-level, EMS, etc. | Control of fixture that the logger is connected to. (Drop-down list)
Fixture Technology | T5, T8, T12, LED, CFL, MV, MH, Induction, incandescent, HPS, LED, halogen, etc. | Lighting Technology being logged (Drop Down list)
Logger Notes |  | Notes specific to logger
Circuit Level
Data Field | Description | Notes
Total Circuit kW (if applicable) | kW or N/A | Total kW of the circuit that logger is metering. Can be either the rated kW if a TOU or the metered kW if a power logger is used.
Circuit Control | Switch, Dimmer, occupancy sensors, day lighting control, EMS, etc. (N/A if logging circuit power) | (Drop down list)
Specific Operating Hours of Circuit | Hours, or N/A if logging circuit power | If there is a specific function or use of the circuit that has specific operating hours that are different from the building/site operating or shift hours.
Circuit Notes |  | Notes Specific to circuit logger is metering
Building/Site Level
Data Field | Description | Notes
Building Type | Office, Hotel/Motel, Hospital, Industrial, School, Retail, etc. | (Drop Down List)
Building Age | Years | To determine vintage
Building Floor Area (sf) | Square feet
Building Address | Company Name, Street, City, State, ZIP | To estimate weather (i.e., interactive effects). Provide ZIP or climate zone if customer information is confidential or cannot be shared
Building Contact Name |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building Contact Number |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building Contact Email |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building Cooling System Applicable to Logger Location | PAC, PTAC, Chiller, Split AC, HP, etc. | Drop Down list. Note that the building can have multiple HVAC systems but this field is for the HVAC system that serves the area where the particular logger is installed, or the particular fixture/circuit that the logger is metering
Building Heating System Applicable to Logger Location | Forced-Air Furnace, HP, Boiler, Electric Resistance, etc. | Drop Down list. Note that the building can have multiple HVAC systems but this field is for the HVAC system that serves the area where the particular logger is installed, or the particular fixture/circuit that the logger is metering
Heating Fuel Type | NG, Electric, Oil, Propane, etc. | Fuel Type of Heating System applicable to logger location. Drop Down list
Building Operating Hours | Hours | Total operating hours of the building/site, including all shifts, and excluding all observed holidays when building is closed
Site Notes |  | Notes specific to site (e.g., area logged is unconditioned but building has HVAC, etc.)
Project/Study Level
Data Field | Description | Notes
Project Name
Project Type | M&V, Load Shape, Custom, Potential, etc.
Project Year | yyyy; yyyy-yyyy | Year project was conducted
Project Sponsor(s) or Client(s) |  | What entity(ies) funded the project/study.
Utility(ies) or Partnership(s) covered/evaluated In project/study
Project Consulting Firms (if applicable) |  | Who carried out the project/study
Consulting Firm Contact(s) | Name, Title, Firm; Name, Title, Firm
Program Name (if applicable) |  | The name of the program or program portfolio being evaluated
Program Type Evaluated (if applicable) | Codes and Standards, Statewide Efficiency, Pilot, etc.
Program Administrator(s)
Program Contact(s) | Name, Title; Name, Title
Project Notes |  | Notes specific to project/study

## Example lighting list
Logger Level | [19 empty] | Circuit Level |  |  |  | Building/Site Level | [11 empty] | Project/Study Level
Logger ID | Raw Logger Data ID | Extrapolated Logger Data ID | Logger Make | Logger Model | Logger Serial Number | Last Calibation Date\Time (if applicable) | NIST Calibration Date\Time (if applicable) | Logging Method | Logging Data Unit | Logging Interval (if applicable) | Date Installed | Date/Time Logging Started | Date/Time Logging Ended | Date Removed | Install Location (Room Type) | Logger kW (if applicable) | Fixture Control | Fixture Technology | Logger Notes | Total Circuit kW (if applicable) | Circuit Control | Specific Operating Hours of Circuit | Circuit Notes | Building Type | Building Age | Building Floor Area (sf) | Building Address | Building Contact Name | Building Contact Number | Building Contact Email | Building Cooling System Applicable to Logger Location | Building Heating System Applicable to Logger Location | Heating Fuel Type | Building Operating Hours | Site Notes | Project Name | Project Type | Project Year | Project Sponsor(s) or Client(s) | Utility(ies) or Partnership(s) covered/evaluated In project/study | Project Consulting Firms (if applicable) | Consulting Firm Contact(s) | Program Name (if applicable) | Program Type Evaluated (if applicable) | Program Administrator(s) | Program Contact(s) | Project Notes
123456D | 123456D_1020 | 123456D_AsmFlr | DENT | D001 | 123456 | 2011-03-03 18:00 | N/A | Power | kW | 0:00 | 2011-10-10 | 2011-10-10 13:30 | 2011-10-20 14:45 | 2011-10-20 | Assembly Floor | 5.43 | Switch | MH |  | N/A | N/A | 6000 | Assembly Floor lighting has different schedule from building | Unconditioned Warehouse | 35 | 35000 | 123 Name Street, City, State, ZIP | John Doe | 555-555-5555 | jdoe@email.com | PAC | FAF | NG | 8760 |  | 2011 C&I Lighting Load Shape Study | Load Shape | 2011 | The States Partnership | The States Partnership | KIMA | Ben Bee, Principal Engineering Consultant, KIMA | N/A | N/A | N/A | N/A
78910H | 78910H_1021 | 78910H_124NameBRs | HOBO | HB001 | 78910 | 2011-03-04 14:00 | N/A | Event | On/off | N/A | 2011-10-11 | 2011-10-11 09:30 | 2011-10-21 09:45 | 2011-10-21 | Bathroom | 0.096 | Occupancy Sensor | T12 |  | 0.192 | Occupancy Sensor | N/A |  | School | 20 | 120000 | 124 Name Street, City, State, ZIP | Jane Joe | 555-555-5556 | jjoe@email.com | Chiller | Boiler | Oil | 2650 |  | 2011 C&I Lighting Load Shape Study | Load Shape | 2011 | The States Partnership | The States Partnership | KIMA | Ben Bee, Principal Engineering Consultant, KIMA | N/A | N/A | N/A | N/A
111213H | 111213H_1022 | Retail125_111213H | HOBO | HB002 | 111213 | 2011-03-05 08:00 | N/A | Interval | % | 0:00 | 2011-10-12 | 2011-10-12 08:34 | 2011-10-22 10:23 | 2011-10-22 | Hallway | 0.076 | Occupancy Sensor | T8 |  | 0.38 | Occupancy Sensor | N/A |  | Retail | 15 | 15000 | 125 Name Street, City, State, ZIP | Dane Moe | 555-555-5557 | dmoe@email.com | HP | HP | Electric | 4000 |  | 2011 C&I Lighting Load Shape Study | Load Shape | 2011 | The States Partnership | The States Partnership | KIMA | Ben Bee, Principal Engineering Consultant, KIMA | N/A | N/A | N/A | N/A
Note on Q2: David Korn: This needs to be clarified, connected kW that an event logger sees may differ from actual metered kW.
Note on AF2: David Korn: This section is insufficient to support heating and cooling interaction.
Note on U3: David Korn: If this is rated kW this should not be NA. For power metering to be meaningful, the fixutres and their rating must be known.
Note on V3: David Korn: This doesn’t seem right. The evaluator must know which lights are controlled by a metered power circuit.

## Refrigeration - General
Component Logger/Trend Data Level
Data Field | Description | Notes
Source of Trend Data | EMS, Contractor-supplied, Metering | Depending on the Trend Data source, other data fields below may not be applicable
Logger ID (if applicable) | SerialM | Unique ID for logger. Serial = logger serial number; M = first character of logger make name (e.g., D for Dent, H for HOBO). If a piece of equipment does not have a logger number, a unique identifier can be established by the provider.
Logger Raw Data ID (if applicable) | SerialM_mmddyy | (If applicable) Unique ID for raw logger file. SerialM = Logger ID (above field); mmdd = logger retrieval day, month, and year.
Extrapolated Logger Data ID or Trend ID (if applicable) | Arbitrary* | (If applicable) *File name can be arbitrary but needs to have unique Logger ID (i.e., SerialM) to identify the logger used to generate the extrapolated data. If Trend data was used, trend ID needs to link to the Unique System ID
Logger Make (if applicable) | DENT, HOBO, MSR, etc.
Logger Model (if applicable) |  | If applicable
Logger Serial Number (if applicable) |  | Serial Number given by manufacturer
Last Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
NIST Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Trend Method | Event, Interval, Instantaneous | Indicates data point type, where Event is a state or TOU trend with no predetermined logging interval, and Interval is a trend with a predetermined logging/sampling interval. The Instantaneous method is for devices taking a single measurement (Drop Down List)
Trend Data Unit | kW, Boolean (0/1; on/off), PSI, degF, Pulse Count | The data point's unit or metric (e.g., power meters record date/time and connected kW every 5 min, event loggers record date/time and on/off state every time there is state change, etc.)
Trend Interval (if applicable) |  | Time format (h:mm:ss)
Date Installed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Date/Time Trending Started (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date/Time Trending Ended (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date Removed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Trend Data Equipment Location | Rack #, Condenser #, Compressor #, Evap Coil #, Walk-in #, etc. | Description of equipment with trend data (Drop down list)
Device Type with Trend Data | Compressor, Condenser, Evap Coil, Compressor Rack, Condenser Fan/Motor, Case, etc. | Description of equipment being metered. (Drop Down List)
Device Make (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Model (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Serial Number (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Nominal Capacity (if applicable) | HP, kBtuh, tons, kW | Different capacity metrics depending on device chosen under Device Type
Device Efficiency (if applicable) | Btuh/Watt, % | Different efficiency metrics depending on device chosen under Device Type
Device Control | Demand (T-stat, pressure gauge), Timer | How device with trend data is controlled
Device Measure Technology (1) |  | Device Measure Technology Drop down list dependent on device type. Place to note efficient technology or practices on refrigeration component
Device Measure Technology (2) |  | Device Measure Technology Drop down list dependent on device type. Place to note efficient technology or practices on refrigeration component
Device Measure Technology (3) |  | Device Measure Technology Drop down list dependent on device type. Place to note efficient technology or practices on refrigeration component
Trend Data Notes |  | Notes specific to trend data
System Level
Data Field | Description | Notes
Unique System ID | Based on site ID in study.
System has remote condensing unit | Yes, No, Both | Both = e.g., mix of walk-ins, display cases and self-contained beverage cases
LT Target Supply Temperature (if applicable) | degF
MT Target Supply Temperature (if applicable) | degF
HT Target Supply Temperature (if applicable) | degF
LT Circuit Suction Temperature (if applicable) | degF
MT Circuit Suction Temperature (if applicable) | degF
HT Circuit Suction Temperature (if applicable) | degF
LT Circuit Capacity (if applicable) | tons
MT Circuit Capacity (if applicable) | tons
HT Circuit Capacity (if applicable) | tons
Total LT Compressor (Rack) Power (if applicable) | HP
Total MT Compressor (Rack) Power (if applicable) | HP
Total HT Compressor (Rack) Power (if applicable) | HP
Total LT Evap Fan Power (if applicable) | HP
Total MT Evap Fan Power (if applicable) | HP
Total HT Evap Fan Power (if applicable) | HP
Total LT Condenser Fan Power (if applicable) | HP
Total MT Condenser Fan Power (if applicable) | HP
Total HT Condenser Fan Power (if applicable) | HP
Regional Average Summer Design Dry Bulb Temperature | degF
LT Minimum Saturated Condensing Temperature (SCT) set point (if applicable) | degF | For Suction lines with separate condensers that may have different minimum SCTs
MT Minimum Saturated Condensing Temperature (SCT) set point (if applicable) | degF | For Suction lines with separate condensers that may have different minimum SCTs
HT Minimum Saturated Condensing Temperature (SCT) set point (if applicable) | degF | For Suction lines with separate condensers that may have different minimum SCTs
Target Saturated Condensing Temp Difference (TD) for LT | degF | ex: 10 degF
Target Saturated Condensing Temp Difference (TD) for MT | degF | ex: 15 degF
Target Saturated Condensing Temp Difference (TD) for HT | degF | ex: 15 degF
Condenser Fan Control Strategy | Fixed Temp, WB Offset | Drop Down
Condenser Fan Fixed or WB Offset Temp | degF
Anti-sweat heater control | Timer, humidity, fixed, DBT, etc. | Drop Down
Anti-sweat heater control set point (if applicable) | Time, RH, degF
Defrost Cycle for LT circuit (if applicable) | electric, hot gas, time off | Drop Down
Defrost Cycle for MT circuit (if applicable) | electric, hot gas, time off | Drop Down
Defrost Cycle for HT circuit (if applicable) | electric, hot gas, time off | Drop Down
Defrost Control for LT circuit (if applicable) | time clock, demand, no control | Drop Down
Defrost Control for MT circuit (if applicable) | time clock, demand, no control | Drop Down
Defrost Control for HT circuit (if applicable) | time clock, demand, no control | Drop Down
Building/Site Level
Data Field | Description | Notes
Savings/Consumption Analysis Methodology | Simulation (DOE2.2R), Regression, Temperature Bin, etc. | Description of how 8760s/metered data is used in energy analysis
Building Type | Grocery Store, Convenience Store, Fast Food Restaurant, Full-Service Restaurant, etc. | (Drop Down List)
Building Age | Years | To determine vintage
Building Floor Area (sf) | Square feet
Building Conditioned Floor Area (sf) | Square feet
Building Refrigerated Floor Area (sf) | Square feet
Building Wall Insulation (Full Assembly) | R-?
Building Ceiling Insulation (Full Assembly) | R-?
Building Address (if applicable) | Company Name, Street, City, State, ZIP | To estimate weather (i.e., interactive effects). Provide ZIP or climate zone if customer information is confidential or cannot be shared
Building Contact Name (if applicable) |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building Contact Number (if applicable) |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building Contact Email (if applicable) |  | This data is contingent on disclosure agreements between parties and is not required by the Protocol
Building (refrigeration) Operating Hours | Hours | Total operating hours of the building/site refrigeration hours, including all shifts, and excluding all observed holidays when building is closed
Project/Study Level
Data Field | Description | Notes
Project Name
Project Type | M&V, Load Shape, Custom, Potential, etc.
Project Year | yyyy; yyyy-yyyy | Year project was conducted
Project Sponsor(s) or Client(s) |  | What entity(ies) funded the project/study.
Utility(ies) or Partnership(s) covered/evaluated In project/study
Project Consulting Firms (if applicable) |  | Who carried out the project/study
Consulting Firm Contact(s) | Name, Title, Firm; Name, Title, Firm
Program Name (if applicable) |  | The name of the program or program portfolio being evaluated
Program Type Evaluated (if applicable) | Codes and Standards, Statewide Efficiency, Pilot, etc.
Program Administrator(s)
Program Contact(s) | Name, Title; Name, Title
Project Notes |  | Notes specific to project/study

## Refrigeration - Specific
Compressor (Rack) Component
Data Field | Description | Notes
Temperature/Circuit Group | LT, MT, HT
Compressor System Type | Stand-alone, Stand-alone w/ VSD, parallel equal multiplex, parallel unequal multiplex
Mechanical Subcooling on Circuit | Yes, No
Refrigerant used | R- | List refrigerant type. Drop Down
# Compressors in Rack
Compressor Rack Sequencing Method (if applicable) | Electronic w/fixed setpoint, etc.
Suction Pressure Control Strategy | Fixed, Floating
Floating Suction Pressure Temp Range (if applicable) | degF
Head Pressure Control Strategy | Fixed, Floating
Floating Head Pressure Temp Range (if applicable) | degF
Specific Compressor Info (below) applies to: | LT circuit, MT, circuit, HT circuit | Example: mid and high temperature compressor racks have compressors of the same make/model/size
Manufacturer
Model Number
Compressor Type | Reciprocating, Screw, Centrifugal, Other, etc.
Motor Efficiency | %
Condensers Component
Data Field | Description | Notes
Condenser Fan Feedback Control | Condenser Sump/Suction Temp, Constant/Fixed, Other..
Saturated Condensing Temperature (SCT) Setpoint | degF
Variable Condensing Setpoint Temp Difference (if applicable) | degF | Target saturated condensing temperature difference above ambient wet-bulb.
Minimum Saturated Condensing Temp (SCT): | degF
Condenser Type | Air-cooled, Water-cooled
Location | Roof, Ground, Conditioned Space
Specific Condenser Info (below) applies to: | LT circuit, MT, circuit, HT circuit
Manufacturer
Model Number
Condenser Efficiency | Btuh/Watt
# Compressors served
Rated Capacity | kBtuh
Fan Control | Single Speed, 2-speed, VSD
# Fans
Total HP of fan motors
Motor Efficiency | %
Cases Component
Data Field | Description | Notes
Type of Case | Reach-in, beverage case, island case, service case, cabinet, coffin-type, walk-in, etc
Condenser Location | Package (self-contained), Remote
Temperature Group | LT, MT, HT | e.g., LT=frozen goods , MT=meats, HT=beverages, cheeses
Length of Case | feet
Width of Case | feet
Height of Case | feet
# Doors on case
Average Length of Door | feet
Average Height of Door | feet
Door Type | Solid, Glass, Both, etc.
Fan Motor Type | PSC, Shaded Pole, ECM, etc.
Number of fans | #
Total Case Fan Wattage | kW, kW/foot
Evap. Fan Control (if applicable) | None (constant), Temp. Setpoint, Defrost Demand | When temp setpoint is satisfied are fans cycled to maintain minimum necessary airflow, or constant, controlled by demand control, etc.
Defrost Control | demand, timer, no control, etc.
Total defrost power | kW | If gas, convert to kW
Average defrost frequency | #/day
Average defrost duration | minutes per defrost
Defrost Fuel | Gas, Electric
Anti-Sweat Heater (ASH) Type | Door electric heater, zero-watt doors | To determine ASH electric load, if applicable
ASH Control Type (if applicable) | Timer, Humidity, constant, N/A
Total Case ASH Wattage (if applicable) | kW
Total Daily ASH Run-time (if applicable) | hrs/day
Display Lighting Technology | T8, T12, LED, CFL, Incandescent, MH, Induction, etc.
Display Lighting Controls | Timer, Occupancy, Switch, Constant (24hrs)
Average Lighting Density | Watts per linear foot

## C&I HVAC
Component Logger/Trend Data Level
Data Field | Description | Notes
Source of Trend Data | EMS, Contractor-supplied, Metering | Depending on the Trend Data source, other data fields below may not be applicable (if raw data is supplied, desirable fields are with *)
Logger ID (if applicable) | SerialM | Unique ID for logger. Serial = logger serial number; M = first character of logger make name (e.g., D for Dent, H for HOBO). If a piece of equipment does not have a logger number, a unique identifier can be established by the provider.
Logger Raw Data ID (if applicable) | SerialM_mmddyy | (If applicable) Unique ID for raw logger file. SerialM = Logger ID (above field); mmddyy = logger retrieval day month, and year.
Extrapolated Logger Data ID (if applicable) | Arbitrary* | (If applicable) *File name can be arbitrary but needs to have unique Logger ID (i.e., SerialM) to identify the logger used to generate the extrapolated data
Logger Make (if applicable) | DENT, HOBO, MSR, etc.
Logger Model (if applicable) |  | If applicable
Logger Serial Number (if applicable) |  | Serial Number given by manufacturer
Last Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
NIST Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Trend Method | Event, Interval, Instantaneous | Indicates data point type, where Event is a state or TOU trend with no predetermined logging interval, and Interval is a trend with a predetermined logging/sampling interval. The Instantaneous method is for devices taking a single measurement (Drop Down List)
Trend Data Unit | kW, Boolean (0/1; on/off), PSI, degF, Pulse Count | The data point's unit or metric (e.g., power meters record date/time and connected kW every 5 min, event loggers record date/time and on/off state every time there is state change, etc.)
Trend Interval (if applicable) |  | Time format (h:mm:ss)
Date Installed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Date/Time Trending Started (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date/Time Trending Ended (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date Removed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Trend Data Equipment Location | Condenser #, Compressor #, Evap Coil #, AH #, etc. | Description of equipment with trend data (Drop down list)
Device Type with Trend Data | Compressor, Condenser, Evap Coil, AH motors, chiller unit, boiler unit, etc. | Description of equipment being metered. (Drop Down List)
Device Make (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Model (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Nominal Capacity (if applicable) | HP, kBtuh, tons, kW | Different capacity metrics depending on device chosen under Device Type
Device Efficiency (if applicable) | AFUE, HSPF, EER, COP, IEER, SEER, kW/ton | Different efficiency metrics depending on device chosen under Device Type
Device Control | Demand (T-stat, pressure, CO2), Timer, Manual, Constant, etc. | How device with trend data is controlled
Efficient Devices (1) | VSD, ECM, Dual-Enthalpy Economizers, etc. | Efficient Devices Drop down list dependent on device type
Efficient Devices (2) | VSD, ECM, Dual-Enthalpy Economizers, etc. | Efficient Devices Drop down list dependent on device type
Efficient Devices (3) | VSD, ECM, Dual-Enthalpy Economizers, etc. | Efficient Devices Drop down list dependent on device type
Trend Data Notes |  | Notes specific to trend data
System Level
Data Field | Description | Notes
Unique System ID | Based on site ID
Cooling Equipment | Air-Cooled Chiller, Water-Cooled Chiller, Absorption Gas/Steam (Chiller/HP), Split DX, Packaged AC, Packaged HP, Mini-Split AC/HP, District Chilled water, etc.
Heating Equipment | Water Boiler, Steam Boiler, Furnace, Packaged HP, Split HP, District Steam, Unit heater, radiant heater, Water-Source Heat Pump, Ground Source Heat Pump, Air Source Heat Pump, etc.
Cooling Capacity | tons, HP, MMBtuh, etc
Heating Capacity | MMBtuh, HP, etc
Overall Cooling System Efficiency | kW/ton; IEER, EER, HSPF, SEER, COP, thermal efficiency (%), etc. | Drop down menu
Overall Heating System Efficiency
Average (Applicable) Temperature Set point for Cooling System, when in use | degF
Average (Applicable) Temperature Set point for Heating System, when in use | degF
Average (Applicable) Temperature set back for Cooling System, when not in use | degF
Average (Applicable) Temperature Set back for Heating System, when not in use | degF
Weekday Cooling Active Schedule
Weekday Heating Active Schedule
Weekend Cooling Active Schedule
Weekend Heating Active Schedule
Cooling Balance Point Temperature | degF | Ambient temperature at which system goes in to active cooling mode
Heating Balance Point Temperature | degF | Ambient temperature at which system goes in to active heating mode
Heating Fuel Type | Gas, Oil, Propane, Electric, Coal, Solar, Wood, etc.
Building/Site Level
Data Field | Description | Notes
Savings/Consumption Analysis Methodology | Simulation (DOE2, Energy Pro), Regression, Temperature Bin, etc. | Description of how 8760s/metered data is used in energy analysis
Building Type | Small Office, Large Office, Restaurant, Retail, Hospital, College Campus, etc. | (Drop Down List)
Building Age | Years | To determine vintage
Building Floor Area (sf) | Square feet
Building Conditioned Floor Area (sf) | Square feet
Building Location | City, State, ZIP | To estimate weather (i.e., interactive effects)
Building (HVAC) Operating Hours | Hours | Total operating hours of the building/site HVAC hours, including all shifts, and excluding all observed holidays when building is closed
Project/Study Level
Data Field | Description | Notes
Project Name
Project Type | M&V, Load Shape, Custom, Potential, etc.
Project Year | yyyy; yyyy-yyyy | Year project was conducted
Project Sponsor(s) or Client(s) |  | What entity(ies) funded the project/study.
Utility(ies) or Partnership(s) covered/evaluated In project/study
Project Consulting Firms (if applicable) |  | Who carried out the project/study
Consulting Firm Contact(s) | Name, Title, Firm; Name, Title, Firm
Program Name (if applicable) |  | The name of the program or program portfolio being evaluated
Program Type Evaluated (if applicable) | Codes and Standards, Statewide Efficiency, Pilot, etc.
Program Administrator(s)
Program Contact(s) | Name, Title; Name, Title
Project Notes |  | Notes specific to project/study

## Process
Component Logger/Trend Data Level
Data Field | Description | Notes
Source of Trend Data | EMS, Contractor-supplied, Metering | Depending on the Trend Data source, other data fields below may not be applicable (if raw data is supplied, desirable fields are with *)
Logger ID (if applicable) | SerialM | Unique ID for logger. Serial = logger serial number; M = first character of logger make name (e.g., D for Dent, H for HOBO). If a piece of equipment does not have a logger number, a unique identifier can be established by the provider.
Logger Raw Data ID (if applicable) | SerialM_mmddyy | (If applicable) Unique ID for raw logger file. SerialM = Logger ID (above field); mmddyy = logger retrieval day month, and year.
Extrapolated Logger Data ID (if applicable) | Arbitrary* | (If applicable) *File name can be arbitrary but needs to have unique Logger ID (i.e., SerialM) to identify the logger used to generate the extrapolated data
Logger Make (if applicable) | DENT, HOBO, MSR, etc.
Logger Model (if applicable) |  | If applicable
Logger Serial Number (if applicable) |  | Serial Number given by manufacturer
Last Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
NIST Calibration Date\Time (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Trend Method | Event, Interval (pulse, kW, kWh, temperature, etc.), Instantaneous | Indicates data point type, where Event is a state or TOU trend with no predetermined logging interval, and Interval is a trend with a predetermined logging/sampling interval. The Instantaneous method is for devices taking a single measurement (Drop Down List)
Trend Data Unit | kW, kWh, Boolean (0/1; on/off), PSI, degF, Pulse Count | The data point's unit or metric (e.g., power meters record date/time and connected kW every 5 min, event loggers record date/time and on/off state every time there is state change, etc.)
Trend Interval (if applicable) |  | Time format (h:mm:ss)
Date Installed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Date/Time Trending Started (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date/Time Trending Ended (if applicable) |  | mm/dd/yyyy hhmm (24 hour format)
Date Removed (if applicable) |  | For loggers that were installed - mm/dd/yyyy
Trend Data Equipment Location | Condenser #, Compressor #, Evap Coil #, AH #, etc. | Description of equipment with trend data (Drop down list)
Device Type with Trend Data | Compressor, Condenser, Evap Coil, AH motors, chiller unit, boiler unit, etc. | Description of equipment being metered. (Drop Down List)
Device Make (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Model (if applicable) |  | If logger is metering a specific modular piece of equipment with Make and model (e.g., single compressor, modular condenser unit)
Device Nominal Capacity (if applicable) | See system level | Different capacity metrics depending on device chosen under Device Type
Device Efficiency (if applicable) | See system level | Different efficiency metrics depending on device chosen under Device Type
Device Control | Temperature, pressure, flowrate, Gas concentration (CO2, NOx), Tank level, Timer, Manual, Constant, etc. | How device with trend data is controlled, If feedback controls what sensor point drives the control algorithm
Efficient Devices (1) | VSD, Design change, Operating point change, etc. | Efficient Devices Drop down list dependent on device type
Efficient Devices (2) | VSD, Design change, Operating point change, etc. | Efficient Devices Drop down list dependent on device type
Efficient Devices (3) | VSD, Design change, Operating point change, etc. | Efficient Devices Drop down list dependent on device type
Trend Data Notes |  | Notes specific to trend data
System Level
Data Field | Description | Notes
Unique System ID | Based on site ID
Process SystemType | Compressed air system, Presses, Machine Tools (Mills, Lathes, etc,), Production cooling or heating, etc. | There are many possible systems and processes, a given study may have no two systems that are the same, therefore this field can be very descriptive text as opposed to standard categories within the study.
System Capacity | Dependent on Equipment Type: Pressure (PSI), Production Rate, Processing Rate, Flowrate, etc. | There are many possible systems and processes, a given study may have no two systems that are the same, therefore this field can be very descriptive text as opposed to standard categories within the study.
Primary System Fuel Type | Gas, Electric, Waste Heat, Coal, Oil, etc.
Overall System Efficiency | Capacity / Primary Fuel Draw at Full Load | There may be a system efficiency curve based on past production and billing data
Primary Energy Consuming Components of System | Pumps, Fans, Compressors, Conveyors, Burners, Electromagnets, etc. | Custom processes may primarily involve applying more standard EE measures such as adding a VSD to component Motors or may involve very customized components within a customized system
Weekday Production Schedule | Volume produced or processed, Pressure maintained, etc. | If 3 shift 24/7, output may be recorded in terms of monthly production if no days with less than 3 shifts
Weekend Production Schedule | Volume produced or processed, Pressure maintained, etc.
Building/Site Level
Data Field | Description | Notes
Savings/Consumption Analysis Methodology | Simulation (DOE2, Energy Pro), Regression, Temperature Bin, etc. | Description of how 8760s/metered data is used in energy analysis
Building Type | Small Office, Large Office, Restaurant, Retail, Hospital, College Campus, etc. | If applicable to process. (Drop Down List)
Building Age | Years | If applicable to process. To determine vintage
Building Floor Area (sf) | Square feet | If applicable to process.
Building Conditioned Floor Area (sf) | Square feet | If applicable to process.
Building Location | City, State, ZIP | If applicable to process. To estimate interactive effects
Building (HVAC) Operating Hours | Hours | See above. Total operating hours of the building/site HVAC hours, including all shifts, and excluding all observed holidays when building is closed
Project/Study Level
Data Field | Description | Notes
Project Name
Project Type | M&V, Load Shape, Custom, Potential, etc.
Project Year | yyyy; yyyy-yyyy | Year project was conducted
Project Sponsor(s) or Client(s) |  | What entity(ies) funded the project/study.
Utility(ies) or Partnership(s) covered/evaluated In project/study
Project Consulting Firms (if applicable) |  | Who carried out the project/study
Consulting Firm Contact(s) | Name, Title, Firm; Name, Title, Firm
Program Name (if applicable) |  | The name of the program or program portfolio being evaluated
Program Type Evaluated (if applicable) | Codes and Standards, Statewide Efficiency, Pilot, etc.
Program Administrator(s)
Program Contact(s) | Name, Title; Name, Title
Project Notes |  | Notes specific to project/study